1188-2 New Mexico

Gas Line Tie-Ins 1-23-01

· Jeff Fawcett Enron-TransWestern

Tel: 713/853-1521

Email: jfawcet@enron.com
· Jeff will provide a budget +/- 30% estimate at their expense to cross tie connections to the TransWestern and El Paso gas lines and bring a single line to the generation plant. A more accurate estimate will require a site visit and will cost.

· To provide the budget estimate Jeff needs:

1. Legal description of the facility – see attached pages

· also per James Topmiller site location: 

latitude: 34o 39’ 24”

longitude: 106o 51’ 42”

2. Linear feet of pipe estimate:

· 8400 ft from TransWestern line to the site fence

· 1000 ft from El Paso line to the site fence

3. Maximum pressure and volume required at the facility:

· initially 3 x GE 6B gas turbines simple cycle – 60,000 lb/h @ 350 psig (300 psig to GT with allowance for scrubber and strainer dP)

· future possible 2 x GE 7FA combined cycle – 130,000 lb/h @ 500 psig (465 psig to GT with allowance for scrubber and strainer dP)

Steve Rutherford

1/23/01

