	[image: image1.png]ENRON




	Engineering Standards
	Standard
	5421

	
	
	Page
	

	[image: image1.png]
	
	1 of 6

	[image: image2.png]OPERATIONS




	STANDARD FOR PURCHASE OF 
	Issue Date
	

	[image: image3.png]



	ORIFICE METER TUBES
	
	06/86

	
	
	Rev. No.
	9

	
	
	Date
	08/95



 1.
SCOPE

 *
This standard establishes the minimum requirements for design, materials and fabrication of orifice meter tubes for natural gas service.  Orifice meter tube testing and inspection shall be performed in accordance with Engineering Standard 5421A in addition to this standard.

 2.
DESIGN AND FABRICATION


2.1
Meter tubes shall be designed and fabricated in accordance with the latest revision of ANSI/API 2530, 49 CFR Part 192 (DOT), the DOT referenced edition of API 1104, and this standard plus all attachments hereto.

 *
NOTE:
ANSI/API 2530, AGA Report No. 3, API 14.3 and GPA 8185 are considered equivalent standards and compliance with any one achieves compliance with the others.

 *
2.2
For minimum design temperatures of -20ºF or higher, meter tubes shall be fabricated from seamless pipe per ASTM A 106 or API 5L and be Grade B, unless otherwise specified.  For minimum design temperatures lower than -20ºF, meter tubes shall be fabricated from seamless pipe per ASTM A 333, Gr 6, unless otherwise specified.

 *
2.3
Pipe I.D. to meet published I.D. within +0.25% out-of-roundness.  Average measurements of sections of pipe preceding and following the orifice fitting by one (1) pipe diameter to be within one half of the above tolerances.

 *
2.4
Orifice fittings, if specified, shall be as follows:

a.
flanged on downstream side and beveled for welding on the upstream side, unless specified otherwise;

b.
bored to match I.D. of meter tube;

c.
carrier and plate to be double-seal, unit type or equal for two-way flow;

d.
complete with two sets of flange taps per AGA Report No. 3 with allowable tolerance for 0.75 Beta ratio.


2.5
If orifice plates are to be supplied by the Vendor, they shall be 316 stainless steel and constructed in accordance with ANSI/API 2530. 


2.6
Vendor shall supply all gaskets and bolting.  Gaskets shall be 1/16" flat ring type meeting ANSI B16.21 and B16.5.  All flange bolt holes shall be two-holed.

*
2.7
All flanges, except at the fitting, shall be weld neck, raised face and shall meet ANSI B16.5 or MSS SP-44.  (Note:  For minimum design temperature less than -20ºF, the flange material shall meet ASTM A350 LF2.)  All paired flanges shall be supplied with ASTM A193, Class B7 alloy steel stud bolts, gaskets and ASTM A194, Gr. 2H, Class II, heavy carbon steel hex head nuts.  (Note: For minimum design temperature less than -20ºF, bolting materials shall be ASTM A320, Gr L7, alloy steel.


2.8
All end closures shall meet either the latest edition of API 6H or ASME Section VIII.  Code stamp or material certifications are not required unless specified otherwise on the purchase order.  All end closures shall be furnished with a safety lock; hinges are not required for sizes 6-inch and less.


2.9
Straightening vanes shall be round, thin-walled tubing, electrically welded at tangent points at both ends.  The tube ends shall be reamed and a 1/4" thick flange welded to the bundle at one end.  The tube bundle shall have external weld lugs to assure tight fit.

 *
2.10
An identification number shall be die stamped (1/4") on the orifice flange on the outer edge near the top of the flange.  The identification number shall consist of the Company's purchase order number with a sequential numerical suffix for each meter ordered and the average inside tube diameter measured one (1) inch upstream of the orifice plate referenced to 68ºF.  The average inside tube diameter measured one (1) inch upstream of the orifice plate referenced to 68ºF shall also be reported as the “Stamped Meter Size” on the “Orifice Meter Tube Calibration Report”, a copy of which is included in this standard.


2.11
Meter tubes shall be blast cleaned to near-white metal and primed with inorganic zinc primer (1.5 mils minimum dry film thickness) and suitably packaged and protected against damage during shipment or storage.  Couplings shall be plugged and ends covered with flange protectors.  Straightening vanes should be installed before shipment.

 3.
TESTING AND INSPECTION

3.1
All circumferential butt welds in gas piping shall be radiographed and found acceptable per API 1104, Section 6.

3.2
All pressure containing portions of meter tubes shall be hydrostatically tested to the minimum pressure specified for a period of at least four (4) hours.

 *
3.3
The orifice meter shall pass the orifice fitting blank plate leakage test prescribed in Engineering Standard 5421A.  Said test shall be performed after the hydrostatic strength test, but prior to the final orifice tube inspection.

 *
3.4
A final orifice meter tube inspection shall be conducted in accordance with Engineering Standard 5421A and the results shall be reported on the “Orifice Meter Tube Calibration Report” as illustrated in this standard, or an approved equivalent form.

3.5
The materials, fabrication and testing shall be subject to inspection and approval by the Company.  Approval or waiver of inspection shall not relieve the Vendor of the responsibility to meet the requirements of this standard.

3.6
Company receiving location shall be notified at least five (5) working days prior to shipment so that the meter tubes may be inspected and micrometer measurements witnessed by a Company representative.

 4.
DOCUMENTATION


4.1
Vendor shall certify that the assembly complies with 49 CFR Part 192 and ANSI/API 2530, that all welding was radiographed and accepted in accordance with API 1104, and that all pressure containing portions of the assembly were pressure tested to the specified minimum test pressure for the specified duration.

4.2
The drawings, certifications and documentation shall be supplied by Vendor as indicated on the specification sheet.


SPECIFICATION SHEET

Location:

Requisition No.

Project:

Project No.

Prepared By:

Approved By:

Date:
Revision:
Revised Date:

Quantity :

Meter No.:

Nominal Pipe Size:

Design Factor (% stress):

Design Pressure (psig):

Design Temperature (°F):

Pipe Wall Thickness:

Pipe Grade:

Ambient Temperature (°F):

Maximum Flow (MMSCFD):

Operating Pressure (psig):

Operating Temperature (°F):

Operating Flow (MMSCFD):

Specific Gravity:

Hydrotest by Vendor (psig):

for four (4) hours minimum duration.

Orifice Plate
( By Vendor:
Plate Thickness 
inches


Tap Bore
inches


Seal Type:  ( Elastomer, ( Teflon

( Not Supplied by Vendor

Orifice Meter Type
( Orifice Flange w/Taps

( Single Chambered Orifice Fitting:  ( Simplex  ( Junior

( Double Chambered Orifice Fitting (Senior)

Meter Tube Dimensions and Configuration per Drawing Attached
( Engineering Standard 5422, Meter Tube without End Closures

( Engineering Standard 5423, Meter Tube with End Closures

( Engineering Standard 5424, Meter Tube for Skid Mounting

( Other:

Drawing/Documentation Quantities:

Approval Drawings


Certified Drawings

 *

Certified Measurements & Data (Use Orifice Meter Tube Calibration Report at the end of this standard or equivalent.)


Compliance Certifications


Pressure Test Data

 *

Blank Plate Leakage Test Data (See Engineering Standard 5421A)

	
	
	
	
	
	
	
	
	
	

	Station

Number
	
	Run

No.
	
	Date

(mmddyy)
	
	
	Company

No.
	060-TW

179-NNG

062-FGT
	012-HPL

018-IGC

028-OPL

	
	
	
	
	
	
	
	
	014-VPL
	172-NBP

	Make
	
	ANSI

Class
	( 300

( 600
	Serial

Number
	
	
	
	000-OTHER
	

	
	
	
	
	
	
	
	
	
	

	Fabricator
	
	Pipe

Schedule
	
	Stamped

Meter Size
	
	
	P.O

Number
	
	

	
	
	
	
	
	
	
	
	
	

	USE DRAWINGS ON BACK OF FORM

FOR MEASUREMENT LOCATIONS
	UPSTREAM TUBE

LOCATION
	MICROMETER READINGS
	DOWNSTREAM TUBE

LOCATION
	

	LOCATION
	A
	B
	C
	D
	E
	F
	G
	

	V
	
	
	
	
	
	
	
	

	LV
	
	
	
	
	
	
	
	

	RV
	
	
	
	
	
	
	
	

	H
	
	
	
	
	
	
	
	

	SURFACE

ROUGHNESS
	
	
	
	
	
	
	
	

	
	
	

	ALLOWABLE AVERAGE
	AVERAGE TUBE ID (Dm at Location (C)
	
	INCHES

	ROUGHNESS = 250 MICROINCHES
	TEMPERATURE OF METER TUBE DURING CALIBRATION
	
	DEGREE F

	PASS
	
	FAIL
	
	
	CALCULATED REFERENCE ID AT 68 DEGREES F (Dm)
	
	INCHES

	
	
	
	
	
	
	
	

	
	
	
	METER TUBE LENGTH
	
	
	

	
	
	ACTUAL TUBE LENGTH PER COMPANY SPECIFICATIONS
	
	

	
	
	
	ANSI/API 2530 FIGURE No. 2-5
	
	
	

	DIMENSIONS
	A
	A’
	B
	C
	C’
	

	MINIMUM REQUIRED
	
	
	
	
	
	

	ACTUAL
	
	
	
	
	
	

	
	** DISTANCE FROM FACE OF PLATE TO FIRST OBSTRUCTION:  THERMOWELL, FITTING, ETC.

	
	
	
	
	
	
	

	
	TYPE
	FLANGED  (
	LINE  (
	
	STRAIGHTENING VANES
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	MAX. L

0.5 C’
	
	INCHES
	MAX.

AREA A
	
	SQUARE

INCHES
	MAX. A

Dr/4
	
	INCHES

	
	
	
	
	
	
	
	
	
	
	

	
	REQUIRED DIMENSION
	MIN. L

10a
	
	INCHES
	
	
	
	
	
	

	
	REF:  ANSI/API 2530 (2-5.5)
	
	
	
	
	
	
	
	
	

	
	ACTUAL DIMENSIONS
	ACTUAL L.
	
	INCHES
	ACTUAL A
	
	SQUARE

INCHES
	ACTUAL a
	
	INCHES

	
	
	
	
	
	
	
	
	
	
	

	
	ORIFICE FITTING
	

	
	
	
	
	
	
	
	
	
	
	

	MAKE
	
	
	TYPE:
	SR (
	JR (
	SIMPLEX (
	FLANGE (
	SERIAL

No.
	
	

	
	
	
	
	
	
	
	
	
	
	

	ALIGNMENT OF

PIPE & FITTING
	OK:

YES/NO
	
	WIDTH OF

PLATE SLOT
	
	INCHES
	WIDTH OF SEAL

W/PLATE
	
	INCHES
	TYPE OF

SEAL
	ELASTOMER  (

	
	
	
	
	
	
	
	
	
	
	TEFLON  (

	
	ORIFICE TUBE ROUNDNESS
	
	
	

	
	REF:  ANSI/API 2530 (2.5.1.3)
	
	
	

	1ST DIAMETER MEASUREMENT REF:  ANSI/API 2530 (2.5.1.3.1.1)
	
	
	
	

	MAXIMUM ALLOWABLE DIFFERENCE UPSTREAM OF ORIFICE = 
	
	Dm X 0.0025 = 
	
	

	
	
	
	
	
	
	

	ANY DIAMETER - Dm = 
	
	PASS
	
	FAIL
	
	

	
	
	
	
	
	
	

	MAXIMUM ALLOWABLE DIFFERENCE FOR ALL UPSTREAM AND DOWNSTREAM MEASUREMENTS = 0.005 X
	
	Dm =
	
	

	
	
	
	
	
	
	

	LARGEST DIAMETER - SMALLEST DIAMETER UPSTREAM =
	
	PASS
	
	FAIL
	
	

	
	
	
	
	
	
	

	LARGEST DIAMETER - SMALLEST DIAMETER DOWNSTREAM =
	
	PASS
	
	FAIL
	
	

	
	
	
	
	
	
	

	REF:  ANSI/API 2530 (2.5.4)
	
	PRESSURE TAPS
	

	
	
	
	

	
	
	
	
	
	
	
	

	DISTANCE FROM
	UPSTREAM
	
	INCHES
	DOWNSTREAM
	
	INCHES
	HOLE DIAMETER ALLOWABLE ± 0.015 INCH

	FACE OF PLATE TO
	
	
	
	
	
	
	
	
	
	
	

	CENTER OF TAP
	PASS
	
	FAIL
	
	PASS
	
	FAIL
	
	
	ACTUAL INCHES
	
	PASS
	FAIL
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	

	COMMENTS:
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	SIGNATURE
	
	
	WITNESS
	
	

	
	
	
	
	
	


CALIBRATION REPORT

DATA COLLECTION SHEET

	UPSTREAM TUBE

LOCATION
	MICROMETER READINGS
	DOWNSTREAM TUBE

LOCATION

	LOCATION
	A
	B
	C
	D
	E
	F
	G

	V
	
	
	
	
	
	
	

	LV
	
	
	
	
	
	
	

	RV
	
	
	
	
	
	
	

	H
	
	
	
	
	
	
	

	SURFACE

ROUGHNESS
	
	
	
	
	
	
	


	
	
	
	

	ALLOWABLE AVERAGE
	AVERAGE TUBE ID (Dm at Location (C)
	
	INCHES

	ROUGHNESS = 250 MICROINCHES
	TEMPERATURE OF METER TUBE DURING CALIBRATION
	
	DEGREE F

	PASS
	
	FAIL
	
	
	CALCULATED REFERENCE ID AT 68 DEGREES F (Dm)
	
	INCHES

	
	
	
	
	
	
	
	


	



	



	

	




* Indicates revised paragraph, this Rev. No.

[image: image2.png][image: image3.png]_868255142

_868255163

_868255088

