AEP Renewable Generation Transmission Projects

Projects have been presented and reviewed by to the ERCOT West Texas Regional Planning Group on March 20, 2001

Thursday, July 19, 2001
Page 1 of 11

From August 1999 through July 2000 there have been requests for 900 MW of wind generation to be interconnected into the West Texas Utilities Transmission system in and around the Rio Pecos region with generation in-service dates between 2/1/01 and 03/01/02. Of the 900 MW requested, there have been interconnection agreements executed for 725 MW and another 60 MW facility is currently being negotiated.. This brings the total amount of generation requesting to be interconnected to 785 MW with all generation being in-service no later than 03/01/2002. 

At present there is 231 MW of generation in-service in the Rio Pecos region, which has a non-coincident  peak load of 138 MW with a current load projection of 162 MW by year 2010. Of the 231 MW of generation, 140 MW is conventional natural gas power located at Rio Pecos, 75 MW is wind generation located on the North Mc Camey to Big Lake 138 kV line, and the last 16 MW is made up of small internal combustion plants and a small combustion turbine located southwest of Rio Pecos.

Today the Rio Pecos region is made up of two 138 kV paths and three 138 kV radial lines. One 138 kV path runs eastward from Rio Pecos to the Twin Buttes 345 kV corridor while the second 138 kV path runs northward from Rio Pecos to the Odessa 345 kV corridor.  Two of the 138 kV radial paths run southwesterly  from Rio Pecos to Ft. Stockton and to 16th Street station with the third radial path running southeasterly from Rio Pecos to Ft. Lancaster.

In order to accommodate the generators’ requests to inject 785 MW into the Rio Pecos region, the study was broken into two parts.  The first part focuses on building the necessary infrastructure required to accept the 785 MW of generation into the local network, and the second focuses on building the necessary bulk transmission paths to transport the generation from the local network to the two 345 kV corridors at Odessa and at Twin Buttes.  Full compliance is maintained with all Transmission Planning Reliability Criteria and Standards set forth by American Electric Power (AEP), Electric Reliability Council of Texas (ERCOT), and the North American Electric Reliability Council (NERC).

The local network improvements can be broken into three triangles: (refer to attached drawing) 
1. Rio Pecos to Crane to North Mc Camey to Rio Pecos

2. Rio Pecos to Ft. Stockton to 16th Street to Rio Pecos

3. Rio Pecos to Mesa View Switch Station to West Yates Switch Station to North McCamey to Rio Pecos

The first triangle requires all three legs to be re-conductored.  The second triangle requires the first leg from 16th Street to Ft. Stockton be converted to 138 kV.  The third triangle requires the first two legs from Rio Pecos to Mesa View Switch and Mesa View Switch to West Yates Switch Station to be re-conductored, and the last leg from West Yates Switch Station to Rio Pecos to be converted to 138 kV. 

The intent of the improvements listed here are to ensure that adequate transmission capacity exists in each of the three triangles to allow the injection of generation into the local network, while maximizing the use of the existing network by minimizing the need for new right-of-way and the need for CCN’s (Certificate of Convenience and Necessity).

Two alternatives were considered for transferring the power from the local network to the 345 kV corridors at Odessa and Twin Buttes. The first alternative added 345 kV lines from Rio Pecos to Twin Buttes, Rio Pecos to Permian Basin, Permian Basin to Moss, and Moss to Odessa. This alternative would require two 138 / 345 kV Autos at Rio Pecos and one 138 / 345 kV Auto at Permian Basin. This alternative is estimated to cost $183 million including the cost of the improvements required for the local network.

The second alternative required re-building two 138 kV paths from Rio Pecos to Odessa, re-building an existing 138 kV line from Rio Pecos to Twin Buttes and adding a third bulk 138 kV path from Rio Pecos to Twin Buttes. The additional bulk path requires two new 138 kV legs from Ft. Lancaster to Friend Ranch and Friend Ranch to Twin Buttes. This alternative is estimated to cost $152 million including the cost of the improvements for the local network.

Given the in-service dates for all wind power generating units is no later than 03/01/02, and the time associated with certifying and building a new 345 kV line and the associated cost, alternative one was neither feasible nor cost effective.  Therefore, the second alternative was selected as the preferred plan, since it provides for timely incremental transmission capacity at an overall lower cost. 

The following information details the criteria violations that result from the interconnection of 785 MW wind farm generation into the Rio Pecos region, and the specific transmission system improvements, and their associated schedule, that have been determined to be necessary to relieve the criteria violations.

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001
Page 2 of 11

__________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


__________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


Project Number 
Title
TP/PM
Type
TSP
Status

TP-2001-011
National Wind Power Wind 
GR
/
BM
IPP
WTU
Proposed

Generation Interconnection

=============================================================================================================

Contingency
Problem
Solution

Rio Pecos to Fort Lancaster 138 kV 
Yates Field area voltages fall 
Addition of a Ft. Lancaster to Friend Ranch 1272 

line and SW Mesa Tap to Big Lake 
below 90% and McCamey to 
ACSR 138 kV line

138 kV
Rankin 69 kV line exceeds its 

emergency rating

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Interconnect National Wind Power's 125 MW
ETN100716
Exempt Line
6/1/01


10472

Over current relay Illinois to Ft. Lancaster
ETN101846
n/a
6/1/02


10458

Add new 138 kV Terminal @ Ft. Lancaster
ETN101847
n/a
9/1/05


9948


Add new 40 mile 138 kV Ft. Lancaster to 
ETN101848
40
To be filed
9/1/05


Friend Ranch (1272 ACSR)
9913

System protection and interrupting devices as 
ETN101849
n/a
9/1/05


result of re-conductors and new lines
9736

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001
Page 3 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


Project Number 
Title
TP/PM
Type
TSP
Status

TP-2001-012
Woodward Wind Generation 
GR
/
BM
IPP
WTU
Proposed

Interconnection

=============================================================================================================

Contingency
Problem
Solution

FPL Energy Power Partner's 
Interconnection
FPL Energy Power Partner's Woodward#1 Wind 

Woodward#1 wind farm
Farm generation in Pecos County

____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Add new 138 kV Terminal at Ft. Stockton
ETN101845
n/a
3/1/03


10478

Interconnect FPL Energy Power Partner's 80 
ETN101850
Exempt Line
4/1/01


MW wind generation facility with RTU / 
10438

Motorized Switch at generation line switch tap

Add new 138 kV line terminal @ Rio Pecos
ETN101855
n/a
9/1/05


10476

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
WTU Crane to TU Crane 138 kV 
Reconfigure WTU/TU Crane substation to a

generation in West Texas - SW Mesa
bus tie  exceeds its emergency 
breaker and half scheme and Replace 138/69

 to Big Lake 138 kV
rating



        kV auto 125 MVA

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Reconfigure WTU/TU Crane substation to a 
ETN101854
n/a
3/1/03


breaker and half scheme and Replace 138/69 
9950

kV auto 125 MVA

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
WTU Crane to Rio Pecos 69kV 
Convert 69 kV North  McCamey to WTU Crane line 

generation in West Texas - Rio 
line exceeds its emergency rating
to 138 kV with 1272 ACSR conductor

Pecos to Crane 138 kV line

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Over current relay Rio Pecos to WTU Crane  
ETN101851
n/a
6/1/02


69 kV
10429

System protection and interrupting devices as 
ETN101852
n/a
6/1/02


result of re-conductors and new lines
10430

Convert 25 miles of 69 kV from North Mc 
ETN101853
25
To be filed
9/1/05


Camey to WTU Crane to 138 kV (1272 ACSR)
9915

 and double circuit from Mc Elroy to WTU 

Crane (795 ACSR)

Convert Spudder Flat 69 kV substation to 138 
ETN101856
n/a
9/1/07


kV
10372


Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001
Page 4 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


Project Number 
Title
TP/PM
Type
TSP
Status

TP-2001-013
King Mnt Wind Generation 
GR
/
BM
IPP
WTU
Proposed

Interconnection

=============================================================================================================

Contingency
Problem
Solution

Upton Wind (King Mountain) Wind 
Interconnection
Upton Wind (King Mountain) Wind Farm generation in

Farm generation
 Crane County

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Interconnect Upton Wind (LP)'s 80 MW King 
ETN101857
Exempt Line
5/1/01


Mnt NW and  80 MW King Mnt SW
10447

Interconnect Upton Wind (LP)'s 80 MW King 
ETN101858
Exempt Line
6/1/01


Mnt NE and  40 MW King Mnt SE
11472

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
WTU Crane to Rio Pecos 138 kV 
Re-conductor 138 kV WTU Crane to Rio Pecos line 

generation in West Texas - Rio 
line exceeds its emergency rating
with 1272 ACSR conductor

Pecos to North McCamey 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Re-conductor 11.5 miles of 138 kV from King 
ETN101861
11.5
Exempt Line
9/1/07


Mnt West Tap to WTU Crane 138 kV (1272 
10404

ACSR)

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
Big Lake 69/138 kV 
Reconfigure Big Lake 138 kV to ring bus

generation in West Texas - Big Lake 
autotransformers exceed their 

138 kV Bus Tie
emergency rating

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Reconfigure Big Lake substation 138 kV bus to
ETN101862
n/a
3/1/04


 five position ring
10482


Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001
Page 5 of 11

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
North McCamey to SW Mesa 138
Re-conductor 138 kV North  McCamey to SW Mesa 

generation in West Texas - Friend 
 kV   line exceeds its emergency 
line with 1272 ACSR

Ranch to Ft. Lancaster 138 kV
rating

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


System protection and interrupting devices as 
ETN101859
n/a
6/1/02


result of re-conductors and new lines
11474

Re-conductor 3.85 miles of 138 kV from SW 
ETN101864
3.85
Exempt Line
3/1/04


Mesa to King Mnt East Tap (1272 ACSR)
11473

Re-conductor 2.0 miles of 138 kV from SW 
ETN101865
2
To be filed
3/1/04


Mesa including King Mnt East Tap at 138kV 
10392

double circuit (795 & 1272 ACSR) to North 

McCamey (795 ACSR)

Reconfigure North Mc Camey 138 kV 
ETN101866
n/a
9/1/05


substation to Ring Bus (five position)
10466

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
SW Mesa to Big Lake 138 kV  line
Re-conductor 138 kV SW Mesa to Big Lake line with 

generation in West Texas - TU Crane
 exceeds its emergency rating
1272 ACSR conductor

 to Odessa EHV 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Install Line Monitoring Equipment on the North 
ETN101860
n/a
3/1/02


Mc Camey to Big Lake 138 kV line
11475

Re-conductor 40.94 miles of 138 kV from SW 
ETN101863
40.9
Exempt Line
9/1/07


Mesa to Big Lake (1272 ACSR)
10384


Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001
Page 6 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


Project Number 
Title
TP/PM
Type
TSP
Status

TP-2001-014
Indian Mesa I Wind Generation 
GR
/
BM
IPP
WTU
Proposed

Interconnection

=============================================================================================================

Contingency
Problem
Solution

Indian Mesa Power Partners I Wind 
Interconnection
Indian Mesa Power Partners I Wind Farm generation 

Farm generation
in Pecos County

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Interconnect Indian Mesa Power Partner's I    
ETN101867
Exempt Line
5/1/01


25 MW wind generation facility
10450

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
Ft. Lancaster 69/138 kV 
Convert 69 kV North McCamey to Mesa View line to

generation in West Texas - Rio 
autotransformer  exceeds its 
 138 kV with 1272 ACSR conductor, add new 

Pecos to Mesa View 138 kV
emergency rating
switching station at Mesa View, add switching station

 at West Yates Tap, and move North McCamey 

138/69 kV autotransformer to West Yates Switch Sta. 

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Install Line Monitoring Equipment on the North 
ETN101868
n/a
3/1/02


Mc Camey to Big Lake 138 kV line
11460

System protection and interrupting devices as 
ETN101869
n/a
6/1/02


result of re-conductors and new lines
11456

Over current relay West Yates Tap to Air 
ETN101870
n/a
6/1/02


Products Tap 69 kV
11449

Add new West Yates 138 kV Switching Station 
ETN101871
Exempt 
9/1/03


(five position ring) and move North Mc Camey
10483
Substation

 69/138 kV auto to West Yates

Add new Mesa View 138 kV Switch Station 
ETN101872
Exempt 
9/1/03


(five position ring)
10480
Substation

Convert Mc Camey 69 kV substation to 138 
ETN101873
n/a
9/1/03


kV
11459

Convert Tippet 69 kV substation to 138 kV
ETN101874
n/a
9/1/03


11463

Re-build 5.57 miles of 138 kV from Mesa View 
ETN101875
5.57
Exempt Line
9/1/05


to Mesa View Switch Station to 138 kV (1272 
11451

ACSR)

Convert 9.98 miles of 69 kV Tippet to West 
ETN101876
9.98
Exempt Line
9/1/03


Yates Switch Station 138 kV (1272 ACSR)
11462

Add new 1.0 mile 138 kV (1272 ACSR) line 
ETN101877
1.0
To be filed
9/1/03


between Yates Pump to Mesa View
11457

Convert 4.23 miles of 69 kV from West Yates
ETN101878
4.23
Exempt Line
9/1/03


 Switch Station to Yates Pump to 138 kV   
11458

(1272 ACSR)

Convert  West Yates Pump 69 kV Substation 
ETN101879
n/a
9/1/03


to 138 kV
11461

Re-build 13.46 miles of 69 kV from North Mc 
ETN101880
30
Exempt Line
8/1/03


Camey to Tippet to 138 kV  (1272 ACSR)
10423


Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001
Page 7 of 11

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
Rio to WTU Crane 69 kV line 
Convert 69 kV Rio Pecos to WTU Crane line to 138 

generation in West Texas - WTU 
exceeds its emergency rating
kV with 1272 ACSR

Crane to Rio Pecos 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Convert 23 miles of 69 kV from Rio Pecos to 
ETN101881
22.98
Exempt Line
9/1/07


WTU Crane 138 kV (1272 ACSR) build .12 
10366

miles of double circuit Crane Tap 1 to WTU 

Crane

Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001
Page 8 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


Project Number 
Title
TP/PM
Type
TSP
Status

TP-2001-015
Indian Mesa II Wind Generation 
GR
/
BM
IPP
WTU
Proposed

Interconnection

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
SW Mesa to Big Lake 138 kV  line
Construct 138 kV Friend Ranch to Twin Buttes line 

generation in West Texas - TU Crane
 exceeds its emergency rating
with 1272 ACSR conductor

 to Odessa EHV 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Over current relay Rio Pecos to Mc 
ETN101883
n/a
6/1/02


Camey 69 kV
11471

Add one new 138 kV terminal at Twin Buttes
ETN101884
Exempt 
9/1/05


10475
Substation

Add two new 138 kV terminals at Friend Ranch
ETN101885
n/a
9/1/05


10477

Add new 70 mile 138 kV line from Friend 
ETN101886
70
To be filed
7/1/05


Ranch to Twin Buttes (1272 ACSR)
10449

=============================================================================================================

Contingency
Problem
Solution

Indian Mesa Power Partners II Wind 
Interconnection
Indian Mesa Power Partners II Wind Farm generation

Farm generation
 in Pecos County

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Interconnect Indian Mesa Power Partner's II   
ETN101882
Exempt Line
10/1/01


135 MW wind generation facility
11470


Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001
Page 9 of 11

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________


Project Number 
Title
TP/PM
Type
TSP
Status

TP-2001-016
Capital Hill Wind Generation 
GR
/
BM
IPP
WTU
Proposed

Interconnection

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
Rio to North McCamey 138 kV 
Re-conductor 138 kV Rio Pecos to North McCamey 

generation in West Texas - Ft. 
line exceeds its emergency rating
line with 1272 ACSR conductor

Lancaster to Mesa View Switching 

Station 138 kV line

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Re-conductor 9.67 miles of 138 kV from Rio 
ETN101894
9.67
Exempt Line
9/1/03


Peocs to North Mc Camey (1272 ACSR)
10387

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
Rio to Mesa View 138 kV line 
Re-conductor 138 kV Rio Pecos to Mesa View 

generation in West Texas - Rio 
exceeds its emergency rating
Switching Station line with 1590 ACSR conductor

Pecos to Capital Tap 138 kV line

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


System protection and interrupting devices as 
ETN101888
n/a
3/1/02


result of re-conductors and new lines
11440

Add 25 MVAR 138 kV Capacitor Bank @ Rio 
ETN101890
25 MVAR 
n/a
3/1/03


Pecos
11439
cap

Upgrade Indian Mesa substation bus to 1590  
ETN101892
n/a
9/1/05


ACSR
11441

Re-conductor 27.13 miles of 138 kV from Rio 
ETN101893
27.13
Exempt Line
12/1/05


Pecos to Mesa View Switch Station ( 1590 
10388

ACSR)

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
Mesa View Switching Station  to 
Re-conductor 138 kV Mesa View Switching Station to

generation in West Texas - Rio 
Ft. Lancaster 138 kV line exceeds
 Ft. Lancaster line with 1272 ACSR conductor

Pecos to Indian Mesa 138 kV
 its emergency rating

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Re-conductor 19.8 miles of 138 kV from Mesa 
ETN101895
19.8
Exempt Line
12/01/06


View Switch to Ft. Lancaster (1272 ACSR)
10396


Prepared by AEP Texas Transmission Planning

Thursday, July 19, 2001
Page 10 of 11

=============================================================================================================

Contingency
Problem
Solution

Addition of 785 MW of wind 
Indian Mesa area voltages fall 
Add 15 MVAR Capacitor Bank @ Mesa View 

generation in West Texas - Rio 
below 90%
Switching Station 138 kV, 15 MVAR Capacitor Bank 

Pecos to Indian Mesa 138 kV line
@ West Yates Switching Station 138 kV, and 15 

MVAR Capacitor Bank @ Ft. Lancaster 138 kV

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Add 10 MVAR and 15 MVAR 138 kV Capacitor 
ETN101889
15 MVAR 
Exempt 
9/1/03


Banks @ West Yates
10360
cap
Substation

Add 10 MVAR and 15 MVAR 138 kV Capacitor 
ETN101891
15 MVAR 
Exempt 
9/1/03


Banks @ Mesa View Switch
10410
cap
Substation

Add 10 MVAR 69 kV Capacitor Bank @ Ft. 
ETN101911
10 MVAR 
n/a
3/1/03


Lancaster
10417
cap

=============================================================================================================

Contingency
Problem
Solution

Capital Hill Wind Farm
Interconnection
Capital Hill Wind Farm generation in Upton County

_____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Transmission Improvement Description
CI IDs
Mileage 
CCN
In-service date


Interconnect Capital Hill 60 MW wind 
ETN101887
Exempt Line
3/1/02


generation facility
10386


Prepared by AEP Texas Transmission Planning


Thursday, July 19, 2001
Page 11 of 11


[image: image1.wmf]North

McCamey



6595



INDIAN MESA I

25

MW





Ft. Lancaster



6579



Mesa View

Switch



6582



-

ORION

125

MW





Indian Mesa



6584



McCamey



6592



SW MESA

75

MW

 Existing



 Big Lake



6535/6536



16th

 Street

Airport



38310



6630



Ft. Stockton



Crane



6615 / 1197



Mid

Kiff



Sw

Rio

Pecos



6601



West

Yates

 Switch





 Friend

Ranch



 Ozon

a



Sonora



Twin Buttes

6011

Sanderson



North Odessa



Odessa

EHV



Sprayberry



Puckett

 Field



38460



 Illinois



6562



Texon

Rankin

Baririlla

 Junction



38460



Puckett

  Tap



Rio

Pecos

 6

98

MW

Rio

Pecos

 4/5

41

MW

1210



1329



1027



1122



6589



6541



60013



6565



6551/6560



Sonora



 69

kV

 Re-conductor / Convert



138

kV

 Re-conductor / Convert



69

kV

 New Circuit



138

kV

 New Circuit

Future Lines and Conversions

for 785

MW's

 requested



New Lines





345

kV



138

kV



69

kV

Morgan Creek

Red Creek

1272

ACSR



24.0 Mile



31.8 Mile



34.4Mile



Spuder

 Flats



12.81 Mile



10.19 Mile



3.85 Mile



40.94 Mile



12.46 Mile



5.53 Mile



9.67 Mile



4.53 Mile



7.6 Mile



4.94 Mile



19.8 Mile



34.4 Mile



50.0 Mile



11.5 Mile



23.0 Mile



5.7 Mile



Static Var

+/- 100

MVAR







Tippet



9.98Mile



23.8 Mile



1.0Mile



WOOD

WRD

 2

80

MW

KING

MNT

 NE

80

MW



KING

MNT

 NW

80

MW



CAPITAL

60

MW



4.53 Mile



2.0 Mile



KING

MNT

 SE

40

MW



KING

MNT

 SW

80

MW



4.23 Mile



1.0 Mile



6583



60015





INDIAN MESA II

135

MW





1272

ACSR



(265

MVA

)



1272

ACSR



(265

MVA

)



1272

ACSR



(265

MVA

)



1272

ACSR



(265

MVA

)



1590

ACSR



1590

ACSR



1272

ACSR



(265

MVA

)



4/0

ACSR



(

39MVA

)



4/0

ACSR



(

39MVA

)



1272

ACSR



(265

MVA

)



1272

ACSR



(265

MVA

)



477

ACSR



(149

MVA

)



477

ACSR



(149

MVA

)



477

ACSR



(149

MVA

)



1272

ACSR

(265

MVA

)



4/0

ACSR



(

39MVA

)



4/0

ACSR



(

39MVA

)



4/0

ACSR



(

39MVA

)



785

MW

 Wind

Proposed Transmission Upgrades





477

ACSR



(149

MVA

)



477

ACSR



(149

MVA

)



477

ACSR



(149

MVA

)



477

ACSR



(149

MVA

)



1590

ACSR



(303

MVA

)



1272

ACSR



(265

MVA

)



1272

ACSR



(265

MVA

)



795

ACSR

(

202MVA

)



WOOD

WRD

 1

80

MW


_1057687337.bin

