October 25, 2000

LVCLP File No. 16.15.11

LVCII File No. 16.19.9


Las Vegas Cogeneration, L.P. and Las Vegas Cogeneration, II L.L.C.
Response to Allegheny (Jones Day) 10/23/00 questions.

Questions for All Facilities

1.  What are the limitations on the number of hours that each facility can

operate and what is the source of those limitations?

LVCLP has no permit limitations on number of operational hours.  LVCII limitation is expected to be 7,920 hours per year for each turbine under the air permit application currently under review.

2.  We understand that there are tentative expansion plans for each

facility.  Were these future expansion plans disclosed to the regulating  agencies at the time that the air permits were applied for, particularly at those facilities which did not undergo PSD review?
There are no expansion plans for either Las Vegas Cogeneration Limited Partnership or Las Vegas Cogeneration II, L.L.C., other than the currently planned construction of the 224 MW (nominal) LVC II generation facility.  The plans for LVCII were disclosed to the regulating environmental agencies.

3.  Which facilities are required to perform continuous emissions

monitoring pursuant to its air permits?  For those facilities performing

CEM, please provide the last two years of data.

LVCLP performs continuous emissions monitoring.  Refer to file no. 14.1.18.2 (attached) for the emissions inventory summary report.  LVCII will also be required to perform continuous emissions monitoring.

4.  Are the facilities FERC jurisdictional for environmental impact

statement purposes pursuant to 18 C.F.R. Part 380?  We noticed that the

only facility with information about this issue was the pipeline at

Lincoln, although the information seemed to suggest that only the pipeline

was subject to the EIS process.  See 2.02.12.G.  Was the rest of the

Lincoln facility subject to the EIS process?  What was the outcome of the

EIS process for the pipeline?

No.

5.  What is Enron's understanding of the process required to transfer the

environmental permits for each facility in connection with the proposed

transaction?  For example, the 1995 stormwater permit for LV Cogen appears

to be triggered by a change in control of the facility.  See 6.02.03 at

page 16.  Do other permits have similar provisions?

The air permit and stormwater permit require notice and consent in the event of a change in control. The draft air permit, section A, item 11 describes the process to change control.  The stormwater permit change in control information is described in section B.2.  The discharge permit does not require notification in the event of change in control.

6.  Will any environmental property transfer or comparable statutes (e.g.

the Illinois Responsible Property Transfer Act) be triggered by the

proposed transaction?

Not applicable in the State of Nevada. 

7. We have reviewed the United States Environmental Protection Agency

comments for the air permit at LV Cogen II, as discussed below.  Did U.S.

EPA provide any additional comments on the air permits for LV Cogen II or

any other facility?

The only EPA comments on the draft air permit for LVCII were those provided to Clark County on September 28, 2000.

LV Cogen

1.  The Industrial User Discharge Permit on Dealbench appears to have

expired on July 1, 2000.  See 6.02.02.  Was it renewed?  If so, please

provide copy.
Refer to attached file 6.2.2.5.

2.  The stormwater discharge permit for LV Cogen appears to be expired.

See 06.02.03.  Was it renewed?  If so, please provide copy.
The agency is behind in issuing the new permit. The agency requested LVCLP to pay the fee and submit the annual report and verbally acknowledged that the permit would continue to be in effect.  LVCLP met the requirements.  Refer to the attached file no. 6.2.3.1 for the Notice of Intent and payment statement to the Bureau of Water Pollution Control.

3.  Does Sunco hold any environmental permits in its own name?  If so,

please provide copies.

Sunco does not hold environmental permits it its own name.

LV Cogen II

1.  EPA contends in its March 23, 1998 and March 24, 2000 letters that BACT

for LV Cogen II was SCONOx and/or XONON.  See 06.01.09.1.   How was this

issue resolved?  Can LV Cogen II meet the 2 ppm NOx limit in the draft

operating permit with the technology that has been proposed?  See 06.01.15.

A BACT analysis of the SCONOX and enhanced SCR technologies was completed for Clark County APCD.  XONOX was not reviewed in detail because it could not match the emission rates of the other technologies.  The extra space needed to use SCONOX was a consideration in SCONOX’s elimination due to the constrained site.  The BACT analysis showed that enhanced SCR was BACT for the project.  The APCD agreed with the determination.

Design studies indicate that LVCII can meet the NOx limit.  Based on GE’s guarantee of 30 ppm NOx from the gas turbine, a SCR efficiency of 94% will be required.  The HRSG manufacturers can include a catalyst bed with this efficiency and will guarantee its performance.

2.  It appears that the State of Nevada has contended that certain

equipment replacement should have undergone new source review in their June 13, 2000 memo.  See 16.03.6.    How was this resolved?  What is EPA's view on this issue?

The air district resolved the issue.  Refer to the Air Permit Technical Support Document, Executive Summary, Concern #1 on Page 4.

[image: image1.wmf]Las Vegas Cogeneration Limited Partnership 

File 14.1.18.2

Facility A00329 Emissions Inventory Summary Report

Permit #

Equipment 

Pollutant

1994

1995

1996

1997

1998

1999

Total (tons)

95 - 99 tons

Annual avg.

Monthly avg.

in tons

in lbs

32901

G.E. LM6000 Turbine

PM10

0.427

0.565

0.606

0.570

0.590

0.524

3.282

2.855

0.571

95.157

CO

2.800

2.400

2.600

5.400

4.800

3.700

21.700

18.900

3.780

630.000

NOx

32.200

32.500

34.800

32.600

37.200

29.600

198.900

166.700

33.340

5556.667

VOC

1.580

2.090

2.240

2.100

2.180

1.935

12.125

10.545

2.109

351.516

SO

X

0.000

0.000

0.000

0.000

0.000

0.000

0.000

0.000

0.000

0.000

NH3

4.300

7.300

8.500

4.400

24.500

24.500

6.125

1020.833

32902

Greenhouse Aux. Boiler

PM10

0.00200

0.01110

0.00251

0.00000

0.00065

0.00680

0.023

0.021

0.004

0.702

CO

0.20000

0.47700

0.10800

0.12000

0.02786

0.68040

1.613

1.413

0.283

47.109

NOx

0.04000

0.08440

0.01910

0.02000

0.00491

0.09072

0.259

0.219

0.044

7.304

VOC

0.01400

0.07530

0.01710

0.02000

0.00439

0.04536

0.176

0.162

0.032

5.405

SO

X

0.00080

0.00443

0.00100

0.00000

0.00026

0.00227

0.009

0.008

0.002

0.265

32903

Greenhouse Aux. Boiler

PM10

0.00130

0.00974

0.00198

0.00000

0.00092

0.00455

0.018

0.017

0.003

0.573

CO

0.14000

0.35100

0.07130

0.16000

0.03974

0.45486

1.217

1.077

0.215

35.897

NOx

0.03000

0.06020

0.01220

0.03000

0.00701

0.06065

0.200

0.170

0.034

5.669

VOC

0.00900

0.06620

0.01340

0.03000

0.00626

0.03032

0.155

0.146

0.029

4.873

SO

X

0.00050

0.00390

0.00080

0.00000

0.00037

0.00152

0.007

0.007

0.001

0.219

A02

Cooling Tower

PM10

1.43

1.42

1.78

1.32

0.899801

6.850

6.850

1.370

228.327

CO

0.00

0.00

0.00

0.00

0.00

0.000

0.000

0.000

0.000

NOx

0.00

0.00

0.00

0.00

0.00

0.000

0.000

0.000

0.000

VOC

0.00

0.00

0.00

0.00

0.00

0.000

0.000

0.000

0.000

SO

X

0.00

0.00

0.00

0.00

0.00

0.000

0.000

0.000

0.000

C01

Diesel Fire Pump

PM10

0.00240

0.00160

0.00000

0.00077

0.00050

0.005

0.005

0.001

0.176

CO

0.00765

0.00510

0.00000

0.00245

0.00159

0.017

0.017

0.003

0.560

NOx

0.03520

0.02350

0.01000

0.01126

0.00732

0.087

0.087

0.017

2.909

VOC

0.00241

0.00161

0.00000

0.00077

0.00050

0.005

0.005

0.001

0.176

SO

X

0.00234

0.00156

0.00000

0.00075

0.00049

0.005

0.005

0.001

0.171

D01

Emergency Diesel Generator

PM10

0.00016

0.00160

0.00000

0.00082

0.00047

0.003

0.003

0.001

0.102

CO

0.00051

0.00510

0.00000

0.00260

0.00151

0.010

0.010

0.002

0.324

NOx

0.00235

0.02350

0.01000

0.01196

0.00069

0.049

0.049

0.010

1.617

VOC

0.00016

0.00161

0.00000

0.00082

0.00048

0.003

0.003

0.001

0.102

SO

X

0.00016

0.00156

0.00000

0.00080

0.00046

0.003

0.003

0.001

0.099

Total (tons)

37.44

40.18

46.28

50.15

54.72

271.22

233.78

Total Plant

annual avg 

(tons)

monthly avg 

(lbs)

PM10

1.950

325.036

CO

4.283

713.889

NOx

33.445

5574.165

VOC

2.172

362.073

SO

X

0.005

0.755

NH3

4.900

1020.833


Page 1 of 1

