
CHANGE ORDER NUMBER 3


(Add Dual Fuel to Unit #2)


to


CONTRACT BD-2-00


By and Between


E-NEXT GENERATION LLC

as Purchaser

Acting through its Agent

ENRON NORTH AMERICA CORP.


AND


GENERAL ELECTRIC COMPANY


as Seller


BLUE DOG PROJECT


(GAS TURBINE GENERATOR PACKAGES)

CHANGE ORDER NUMBER 3

(Gas Turbine Generator Contract)

PART I  REQUIREMENTS

1.
In accordance with Contract Article XI of Contract BD-2-00 between General Electric Company ("Seller") and E-Next Generation LLC ("Purchaser"), dated May 31, 2000, (the "Agreement"), Purchaser acting through its Agent, Enron North America Corp., hereby amends the Agreement to include all changes set forth in this Change Order Number 3.

2.
Summary of Change:  Pursuant to Section 11.2 of the Agreement, Agent directs and Seller agrees to change the fuel system in Unit #2 from single to dual fuel (gas and liquid fuels) in accordance with the following requirements:

2.1
Purchaser's fuel shall meet the requirements of Seller's liquid fuel specification GEI 41047H set forth in Attachment 2 hereto.

2.2
Seller shall amend applicable drawings and documents to reflect the change to a dual fuel system.

2.3
As a Specific Performance obligation, Seller guarantees that the Adjusted Net Electrical Output, Adjusted Net Heat Rate, and Adjusted Emissions of Unit #2, as defined in the Contract, except in this case when operated on liquid fuel having the composition specified in Attachment 3 hereto and tested in accordance with a liquid fuel Test Procedure (to be mutually agreed), shall meet or exceed the guaranteed liquid fuel performance values for Net Electrical Output, Net Heat Rate, and Emissions as set forth in Attachment 7 hereto.

2.4
The mutually agreed Performance Test Procedures for demonstration of Electrical Output and Heat Rate on natural gas and liquid fuel shall be based on the Performance Test Guidelines set forth in Attachment 4 hereto, which shall supersede in whole, the guidelines set forth in Exhibit F of the Contract.

2.5
Additional Basis Conditions relevant to Seller's performance guarantees on liquid fuel are as set forth in Attachment 5 hereto.

2.6
The mutually agreed Emissions Test Procedures for demonstration of Emissions on natural gas and liquid fuel shall be based on the Emissions Test Guidelines set forth in Attachment 6 hereto, which shall supersede in whole, the guidelines in Exhibit F-2 of the Contract.

3.
Changes to the Agreement: Delete the current Exhibit N-1 and replace it with the Exhibit N-1 attached hereto as Attachment 1 and hereby made part of this Change Order through this reference.


PART II COST
Revised Purchase Amount: The lump sum amount added to the Purchase Amount by this Change Order is one million, four hundred forty five thousand U.S. dollars ($1,445,000.00).  Summary of the Purchase Amount through this Change Order Number 3 is as follows:

Original Purchase Amount




USD 37,656,200

Purchase Amount through Change Order number 1
USD 38,634,200

Purchase Amount through Change Order number 2
USD 39,103,200

Purchase Amount as of this Change Order Number 3
USD 40,548,200


PART III TERMS AND CONDITIONS
1.
The terms and conditions of this Change Order number 3 are as set forth in the Agreement as amended by Change Orders number 1 and 2, except as otherwise amended pursuant to the terms of this Change Order number 3.

2.
The effective date of this Change Order Number 3 shall be March 12, 2001.

3.
All other terms and conditions of the Agreement not changed by this Change Order remain in full force and effect.

Enron North America Corp.

As Agent for E-Next Generation LLC

as Purchaser

By:
                                                

Title:                                                  

Date:
                                                  
and

General Electric Company 

as Seller

By:
                                                  
Title:
                                                  
Date:
                                                  
Attachment 1 to Change Order 3

EXHIBIT N-1  PURCHASE AMOUNT RECONCILIATION Revision 3
	Item
	U.S. Dollars

	Base Price for each Unit
	$19,117,500

	Total Base Price (for two Units)
	$38,235,000

	Transportation Deduct/Option
	($198,000/unit)

	Export Packing Deduct/Option
	($83,400/unit)

	Open Cooling Water System vs Closed
	$9,000

	2 Stage Static Filtration vs. Self Cleaning
	$9,000

	Eliminate APU
	($16,000)

	Open ventilated Generator vs. TEWAC Generator
	$0

	65 kVA bus bracing vs 42 kVA
	$1,700

	Historian (1 total)
	*$130,000

	<I> to <HMI> $35K/HMI x 3HMIs
	*$105,000

	Interconnecting cables for PEECC
	$67,800

	Galvanized air filter support steel
	$5,900

	Air Filter Interior Lighting
	$9,400

	Peak Load Capabiliy
	$11,000

	Pull out PT=s
	$6,100

	Bleed Heat Piping
	$31,400

	Generator curves on HMI
	$3,700

	Delete Switchgear compt (Generator Breaker), add GLAC
	($325,000)

	Add CT=s (5 per Unit)
	$11,000

	96M Multitransducer
	$13,800

	27TN Relay (Stator Ground Fault)
	$9,800

	Didode Fault Monitor
	$1,900

	Flux Probe
	$6,900

	Monitor Brush Rigging
	$13,700

	Smoke Detector in Collector Compartment
	$1,400

	Dual element RTD=s in gas generator path
	$700

	3-phase collector heaters
	$1,300

	Inlet Chiller Coil Space for each Unit
	$489,000

	Storage and Preservation of Unit #1 through June 30, 2001
	$469,000

	Change Unit #2 to dual fuel 
	$1,445,000

	
	


	
	

	Cost Attributable to Unit #1
	$19,786,100

	Cost Attributable to Unit #2
	$20,762,100

	Total (the Purchase Amount)
	$40,548,200


ATTACHMENT 2  LIQUID FUEL SPECIFICATION GEI 41047H

ATTACHMENT 3  LIQUID FUEL COMPOSITION

Supplemental to Exhibit A-1 of the Contract:

ATTACHMENT 4  PERFORMANCE TEST GUIDELINES FOR LIQUID FUEL

ATTACHMENT 5  LIQUID FUEL BASIS CONDITIONS

Supplemental to Exhibit A of the Contract

ATTACHMENT 6  EMISSIONS TEST GUIDELINES FOR LIQUID FUEL

ATTACHMENT 7  LIQUID FUEL PERFORMANCE GUARANTEED DATA

ESTIMATED PERFORMANCE   PG7121(EA) 
Load Condition 

BASE 


Exhaust Pressure Loss 
 inches Water 
5.19 


Ambient Temp. 
 Deg F. 
77. 


Output 
 kW 
80,900. 


Heat Rate  (LHV) 
 Btu/kWh 
11,060. 


Heat Cons. (LHV) X 106 
 Btu/h 
894.8 


*Auxiliary Power 
 kW 
 460 


Output  Net 
 kW 
80,440. 


Heat Rate (LHV)  Net 
 Btu/kWh 
11,123. 


Exhaust Flow   X 103
 lb/h 
2285. 


Exhaust Temp. 
 Deg F. 
1006. 


Exhaust Heat (LHV) X 106 
 Btu/h 
545.7 


Water Flow 
 lb/h 
37,540. 
 

EMISSIONS 
NOx 
 ppmvd @ 15% O2 
42. 


NOx AS NO2 
 lb/h 
157. 


CO 
 ppmvd 
20. 


CO 
 lb/h  
41. 


UHC 
 ppmvw 
7. 


UHC 
 lb/h  
9. 


Particulates 
 lb/h 
10.0 


   (PM10 Front-half Filterable Only)

EXHAUST ANALYSIS      % VOL. 

Argon 

0.87 


Nitrogen 

73.08 


Oxygen 

13.17 


Carbon Dioxide 

4.47 


Water 

8.42 
 

SITE CONDITIONS 
Elevation 
 ft. 
250.0

Site Pressure 
 psia 
14.57

Inlet Loss 
 in Water 
3.5

Exhaust Loss 
 in Water 
5.5 @ ISO Conditions

Relative Humidity 
 % 
60

Fuel Type 
  
Distillate, H/C Ratio of 1.8 


Fuel LHV 
 Btu/lb  
18300 @ 80 °F 

Application 
 
7A6 Air-Cooled Generator

Combustion System 
 
9/42 DLN Combustor

Emission information based on GE recommended measurement methods. NOx emissions are corrected to 15% O2 without heat rate correction and are not corrected to ISO reference condition per 40CFR 60.335(c)(1). NOx levels shown will be controlled by algorithms within the SPEEDTRONIC control system.  

Distillate Fuel is Assumed to have 0.015% Fuel-Bound Nitrogen, or less.

FBN Amounts Greater Than 0.015% Will Add to the Reported NOx Value.

*Previous Performance quotes on natural gas did not include associated distiallte auxiliary losses

IPS-         
version code-  2 . 4 . 0   Opt: N     71210696

MOOREKE
3/13/01 15:09
77F_60RH-dist-guarantee.dat

Contract BD-2-00 rv 7e

5
CHANGE ORDER 3 (Rev-1)  3/16/01

