
Turbine Curtailment


May 6, 2002  Version 1.00

Software Description


Turbine curtailment software stops and starts wind turbines for the following conditions: energy output for a group of turbines, wind direction, wind speed, and time of day.


Curtailment parameters are protected by passwords where each user can be given different capabilities.  One user could be given authority to modify the energy curtailment parameters and not allowed to modify direction curtailment values, while another user allowed to change the direction curtailment values and not allowed to modify the energy curtailment parameters.


The curtailment software is made up of two parts, a user interface program and a service program.  The service program receives data from the turbines, decides if any turbines should be curtailed, and sends the curtailment commands to the turbines.    The user interface program communicates to the service program and allows the user to view and modify the conditions of when curtailment occurs.

This software is designed to function with the Visupro software.  It receives turbine and met tower data from Visupro, and issues the turbine curtailment message to Visupro.  Visupro then stops or starts the turbine based on what it receives from this program.

On computer reboot the program will wait 10 minutes before sending any curtailment commands.  This is done so that the program has time to calculate the 10-minute average wind speed and direction that is needed to make a curtailment decision.

Status Screen

[image: image14.jpg]‘ Not authorized to make changes

o





Status screen shows the turbine’s curtailment status, real-time power output, ten minute average power output, real-time wind speed, ten minute average wind speed, and if a met tower is connected to the turbine then it shows the real-time and ten minute average wind speed and wind direction data for the met tower.

The curtailed column will be one of the following:  

Blank

( Turbine is not curtailed

Energy

( Energy curtailed

Direction
( Wind direction curtailed

Time

( Time of day curtailed

Wind

( Wind speed curtailed

Com Loss
( Turbine not communicating to program

Energy Curtailment

[image: image2.jpg]Fie Securty Help

tatus Eneiy | Dicoton| Tine of oy | Wind speed| Evcuce

a1

Total
Tubines

Tubines
Orine.

3 450

Moy Groups

00

623

Group Name: [Group-T MasMuw: [10.00
Startcurtaiment | End cutaiment






Energy curtailment occurs when the 10-minute average MW and real time MW readings for the group are above the set point.  When a group needs to be curtailed, turbines are randomly selected for curtailment.

Energy curtailment ends when the 10-minute average MW and real time MW readings for the group are 1 MW or more below the set point, and the turbine has been curtailed for at least 10-minutes.

To change the energy curtailment set point for a group:  Click on the group to be changed, enter the new set point in the “Max MW” box, and click the “Start curtailment” button.  The max MW for a group can not be less then 10 MW.

To end energy curtailment for a group:  Click on the group, then click the “End curtailment” button.

[image: image1.jpg]=18l

Fie Securty Help

(5885 Enege| Diection | Time of day| Wid speed| Exchce]

RealTme | 10Min | RealTime | 10Min | RealTime | 10Min | RealTime | 10Min
Tutine Power | Power | Wind | Wind | Metwind| MetWind| MetDi | MetDi
1P| Number | Cutaled | kw) (k) /s) /s) /s) /s) (Deg) | (Deg)

2 840001007 14300 1410 1800 125

250 840001003 160100 1s0054 1540 1261 1880 1228 2500 2500





After clicking either the start or end curtailment button, the following screen will appear asking you to notify the site of the curtailment change.

After notifying the site click the “Execute Change” button to activate the new curtailment setting.  If the “Execute Change” button is not pressed the change will take place after nine minutes.

To add, change, or delete turbine groups click on the “Modify Groups” button on the energy curtailment screen.

[image: image8.jpg]1B

Notiy ste personelof cutaiment change,

and then olck the "Execute Change” bulton,
The cutsiment change wil automaticaly take

place after 3 minutes evenif the "Execute.
buton s ot pressed.

| Evecute Change |





To change a existing group of turbines:  Click on the group, add or remove turbines from the group, and click the “Save” button.

To delete a group:  Click on the group, and then click the “Delete” button.

To create a new group:  Click on the blank group line, type in a new group name into the “Group Name” box, add turbines to the group, and then click the “Save” button.

Direction Curtailment

[image: image3.jpg]Turbine Curtailment

Fie Securty Help

ot Energy Diecton | Tine ofcay | wind speed| Evcue

~=lolx|

Tutine

280001007 281

T~ Enable Direction Curtaiment

Cursiment enzbled
10.30 wind speed (m/s)

[ Minimum cutsinert

time (minutes)

Cutal #1] Cutal #1
ToDeg | FromDeg

Fiom Deg

. &0,

Tubine:

Ditection

Fiom Deg Fiom Deg

Ditectior:

Fom ETN oes
Te Elves

Fon E oes
M oes

T

Ditection:

Fon [ 0es
Te e

Ditestior:

o [ 0es
te e

Save





A turbine is curtailed when the 10-minute average wind direction measured from a nearby meteorological tower is within the specified curtailment direction range, and the 10-minute average wind speed measured from the nacelle anemometer is above the minimum wind speed set point value.  Once a turbine is curtailed it will remain curtailed for at least the minimum curtailment time.

To enable the program to do direction curtailment the box “Enable Direction Curtailment” must be checked.

“Curtailment enabled wind speed” box sets the value at which the wind speed must be above for direction curtailment to be allowed.

“Minimum curtailment time” is the number of minutes that a turbine must stay curtailed once it is curtailed for wind direction.

To add a turbine to the direction curtailment list.

a. Select a turbine from the drop down list “Turbine”.

b. Select a Met. Tower from the drop down list “Met Tower”.  

The Met. Tower is used to determine when the turbine should be curtailed for wind direction.

c. Enter the direction ranges that this turbine should be curtailed.

The direction ranges run in a clockwise direction.  (If you enter 350 in the “From” box and 10 in the “To” box, then the turbine would be curtailed for directions from 350 to 360 degrees, along with the direction 0 to 10 degrees).

d. Click the “Save” button to add the turbine to the curtailment list.

To delete a turbine from the direction curtailment list.

a. Click on the turbine to be removed from the curtailment list.

b. Click the “Delete” button.

To change the values for a turbine on the direction curtailment list.

a. Click on the turbine to be modified in the curtailment list.

b. Make changes to the direction ranges or met tower number.

c. Click the “Save” button.

Time of Day Curtailment

[image: image4.jpg]=18l

T e i
Stous | Eners| Diecon Tinef o | win peed] e |

Tubine

Tubine:

Stant Time: [10:00008M =1
End Tine: [120000PM =





Time of day curtailment curtails turbines based on the time of day.

To add a turbine to the time of day curtailment list 

a. Click on the blank line in the “Time of day curtailment” list.

b. Select a turbine from the “Turbine” drop down list.

c. Select the time that the curtailment should start from the “Start Time” box.

d. Select the time that the curtailment should end from the “End Time” box.

e. Click the “Save” button.
To change the curtailment time for a turbine on the time of day curtailment list 

a. Click on the turbine in the “Time of day curtailment” list to be changed

b. Modify the start and end curtailment time 

c. Click the “save” button

To delete a turbine from the time of day curtailment list 

a. Click on the turbine in the “Time of day curtailment” list

b. Click the “Delete” button

Wind Speed Curtailment

[image: image5.jpg]e
tats| Energ| Dicston| Tine of ey Windspeed | Evcuce |

Tubine

Tutine:

Cunalf wind
Wind Speedt [300





Wind speed curtailment curtails a turbine when the 10-minute average wind speed measured from the turbine anemometer, is either above or below the specified value.

To add a turbine to the wind speed curtailment list 

a. Click on the blank line in the “Wind speed curtailment” list.

b. Select a turbine from the “Turbine” drop down list.

c. Select whether the turbine should be curtailed above or below the wind speed

d. Enter the curtailment wind speed

e. Click the “Save” button.
To change the curtailment values for a turbine on the curtailment list 

a. Click on the turbine in the “Wind speed curtailment” list to be changed

b. Modify the curtailment values 

c. Click the “save” button

To delete a turbine from the curtailment list 

a. Click on the turbine in the “Wind speed curtailment” list

b. Click the “Delete” button

Exclude from Curtailment

[image: image6.jpg]Turbine Curtailment

Fie Securty Help

tats| Enorg| Dicston| Tine fcay | Windspeed e |

Tutbines on tis st are excluded
from any cusient

Tubine:

~=lolx|





The curtailment exclude list is to be used for turbines that are under testing, or other temporary conditions where you currently do not want a turbine to be curtailed.

To add a turbine to the exclude list select it from the “Turbine” drop down list, and click the “Save” button.

To remove a turbine from the exclude list select it from the list, and click the “Delete” button.

Program Configuration

[image: image7.jpg]| - contigure =Tk

PC Number 840414250 ot = ste rumber) [840000250

Cutaiiment broadsastrterval (seconds] [10
Local Netwark IP addess: [192.1680.253 =

Path to Database fies:

€ WisuprohTibCurtal
Save





Enter the program configuration screen by clicking on the “File” menu item and selection “Configure”.

PC number 840xxx250” (xxx = site number)

The first 3 digits of this number is the country code that this site is located in, 840 is the country code for the United States.  The second group of 3 digits is the site number, and the ending 3 digits of this number is the final part of the computer’s IP address.  Example: If this site is in the U.S., the site number is 7, and the IP address of the computer is 192.168.0.250, then the PC-number would be 840007250.

Curtailment broadcast interval (seconds)

Enter the number of seconds between each curtailment broadcast message.

Local IP address

Select from the drop down list box the computer’s IP address that is part of the turbine network.  This box normally has only 1 choice, but there will be more then one choice if multiple network cards are installed in the computer.

Path to Database Files

Enter the location of where the database files should be saved.

Security

[image: image9.jpg]=lolx|

Grown

Group2

Total
Tubines

Group Name:[Group-1

Group Lit
1) 840001001
2) 340001007
250) 340001003

Tubine st




Logon screen

To make changes to the program settings you must be logged in.  Click on the “Security” menu item, and select “Logon”. 

[image: image10.jpg]‘ Need tologon

&




User accounts

To add, remove, or modify a user’s access click on the “Security” menu item and select “User List”

To add a new user.

a. Enter a user name in the “Name” box.

b. Enter the user’s password in the “Password” box. 

c. Select the user’s access rights.

d. Click the “Save” button to add the user.

To remove a user.

a. Click on the user to be removed.

b. Click the “Delete” button.

To modify a user’s password or access rights.

a. Click on the user to be modified.

b. Make the needed changes.

c. Click the “Save” button.

[image: image11.jpg]secoriy

serbame: [
Passwort |

w ] el |





You will receive this message if you try to make a change, but are not logged in.

[image: image12.jpg]BT oo

Name:

Passward: [4543

Doe

= |

s |

User Level [P
[Admin El W
St Rl

UserAcsess——————

¥ Energy Cutaiment
I¥ Diection Curtaiiment

¥ Wind speed Cutaiment
[ Time of day Cutaiment
T~ Administrator Functions




You will receive this message if you are attempting to change an item that you have not been authorized to modify.

About

[image: image13.jpg]TibCutal.exe
Version 1.00
Copyight 2002

Cutal tutbines based on
power output, wind diecton,
Wind speed, o time of da.




Program’s “About” screen

To see the program’s version level, click on the “Help” menu item and select “About”

Program Files

Curtailyyyymm.db
( Logbook of program activity (yyyy = Year, mm = Month)

CurtailDbPwr.db
( Power curtailment parameters

CurtailParms.db
( Direction, Time of day, and wind speed curtailment parameters

UserAccts.db
( User access list

TrbCurtail.ini
( Screen position and size

Logbook Entries in Curtailyyyymm.db file
Message
Message Description

TrbCurtail Service Started
TrbCurtail Service software started.  Curtailment software is now able to curtail turbines as needed

TrbCurtail Service Stopped
TrbCurtail Service software stopped.  Curtailment software is no longer able to curtail turbines

Dir Curtail Met: xx) yyy
Turbine assignment changed to use this met tower for determining when to perform direction curtailment – Turbine name stored in the  “SystemNumber” field 

Dir Curtail #x: yyy - zzz
Direction curtailment range changed for turbine – Turbine name stored in the  “SystemNumber” field

Dir Curtailment removed
Turbine removed from direction curtailment list – Turbine name stored in the  “SystemNumber” field

xxxx group max MW Changed: yyy
Maximum MW for group changed

xxxx curtailment ended
Energy curtailment for group ended

Added to group: xxxx
Turbine added to energy curtailment group – Turbine name stored in the  “SystemNumber” field

Removed from group: xxxx
Turbine removed from energy curtailment group – Turbine name stored in the  “SystemNumber” field

Added to curtailment exclusion list
Turbine added to curtailment exclusion list – Turbine name stored in the  “SystemNumber” field

Removed from curtailment exclusion list
Turbine removed from the curtailment exclusion list – Turbine name stored in the  “SystemNumber” field

Wind speed curtailment disabled
Wind speed curtailment for turbine disabled – Turbine name stored in the  “SystemNumber” field

Wind speed curtailment set to curtail below setpoint
Wind speed curtailment for turbine set to curtail turbine when wind speed is below set point – Turbine name stored in the  “SystemNumber” field

Wind speed curtailment set to curtail above setpoint
Wind speed curtailment for turbine set to curtail turbine when wind speed is above set point – Turbine name stored in the  “SystemNumber” field

Wind speed curtailment set to x m/s
Wind speed curtailment set point for turbine changed to a new value – Turbine name stored in the  “SystemNumber” field

Time curtailment x:x – y:y
Time curtailment for turbine changed – Turbine name stored in the  “SystemNumber” field

Time curtailment disabled 
Time curtailment for turbine disabled – Turbine name stored in the  “SystemNumber” field

PC Number changed to: xxx
The pc number used in the curtailment software has been changed

Local IP changed to: w.x.y.z
The IP address that the curtailment uses to communicate to the turbine network has been changed

Broadcast rate changed to: x
The rate at which the curtailment software sends out the curtailment messages to the turbines has been changed

Min dir curtail time changed to: x
The amount of time that a turbine must stay stopped once curtailed for direction has been changed.

Min Pwr curtail time changed to: x
The amount of time that a turbine must stay stopped once curtailed for energy has been changed.

Min dir curtail WS changed to: x
Direction curtailment enable wind speed changed.

Dir curtail enabled changed to: x
Direction curtailment Enabled / Disabled

Data file path changed
Path to data files changed

Turbine Com Loss
Communication loss to turbine – Turbine name stored in the  “SystemNumber” field

Met Com Loss
Communication loss to Met Tower – Met Tower name stored in the  “SystemNumber” field

Turbine Com Established
Communication established to Met Tower – Met Tower name stored in the  “SystemNumber” field

Met Com Established
Communication established to Met Tower – Met Tower name stored in the  “SystemNumber” field

Energy curtailed
Turbine curtailed for energy – Turbine name stored in the  “SystemNumber” field

Direction curtailed
Turbine curtailed for direction – Turbine name stored in the  “SystemNumber” field

Wind speed curtailed
Turbine curtailed for wind speed – Turbine name stored in the  “SystemNumber” field

Time curtailed
Turbine curtailed for time of day – Turbine name stored in the  “SystemNumber” field

Energy un-curtailed
Turbine un-curtailed for energy – Turbine name stored in the  “SystemNumber” field

Direction un-curtailed
Turbine un-curtailed for direction – Turbine name stored in the  “SystemNumber” field

Wind speed un-curtailed
Turbine un-curtailed for wind speed – Turbine name stored in the  “SystemNumber” field

Time un-curtailed
Turbine un-curtailed for time of day – Turbine name stored in the  “SystemNumber” field




Database File Layouts

Curtailyyyymm.db

Logbook of Program Activity (yyyy = Year, mm = Month)



Item
Field Name
Field Description
Field Type

1
Index
Sequential number
Auto increment

2
IP
Turbine ID (Last part of IP address.  (IP=192.168.0.1 ( then IP would be 1)
Integer

3
SystemNumber
Turbine name
String 10 bytes

4
Date
Local Date
Date

5
Time
Local Time
Time

6
TimeOffset
Number of seconds between Local time and UTC time
Integer

7
User
User Name
String 20 bytes

8
Msg
Message
String 40 bytes

CurtailParms.db

Direction, Time of day, and wind speed curtailment parameters



Item
Field Name
Field Description
Field Type

1
Index
Sequential number
Auto increment

2
TrbID
Turbine ID (Last part of IP address.  (IP=192.168.0.1 ( then TrbID would be 1)
Integer

3
ExcludeFlg
Turbine on curtailment exclude list
Integer

4
MetID
Met tower ID (Last part of IP address.  (IP=192.168.0.1 ( then MetID would be 1)
Integer

5
FromDir1
Direction #1  From direction
Float

6
ToDir1
Direction #1  To direction
Float

7
FromDir2
Direction #2  From direction
Float

8
ToDir2
Direction #2  To direction
Float

9
FromDir3
Direction #3  From direction
Float

10
ToDir3
Direction #3  To direction
Float

11
FromDir4
Direction #4  From direction
Float

12
ToDir4
Direction #4  To direction
Float

13
WsCurtFlg
Curtail for wind speed (0=No, 1=Below, 2=Above)
Integer

14
WsCurtail
Wind speed curtailment value
Float

15
STmCurtail
Time of day curtailment -start time
Time

16
ETmCurtail
Time of day curtailment -end time
Time

CurtailDbPwr.db

Power curtailment parameters



Item
Field Name
Field Description
Field Type

1
Index
Sequential number
Auto increment

2
TrbID
Turbine ID (Last part of IP address.  (IP=192.168.0.1 ( then TrbID would be 1)
Integer

3
GroupName
Name of energy curtailment group
String 10 bytes

4
MaxMW
Maximum MW
Float

UserAccts.db

User access list



Item
Field Name
Field Description
Field Type

1
Index
Sequential number
Auto increment

2
User
User Name
String 20 bytes

3
Pw
User password (encrypted) Maximum password size 10 bytes
String 20 bytes

4
AccessLevel
User’s access level (bit waited)
Integer

Visupro to Turbine curtailment program communication

Curtailment Network port: '7200' udp

Structure of data received from turbines:


TCurtailPlantData = packed record

    

MsgType
: LongWord;
// Message type



MsgVersion
: BYTE;
// Message version (1)



IDNo
: String[10];
// Plant ID



StateBits
: LongWord;
// Status



Para1
: Double;
// Parameter 1



Para2
: Double;
// Parameter 2



Para3
: Double;
// Parameter 3



Para4
: Double;
// Parameter 4



Para5
: Double;
// Parameter 5



Para6
: Double;
// Parameter 6



Para7
: Double;
// Parameter 7



Para8
: Double;
// Parameter 8


end;

Message Type:



Plant = $01001001

Met   = $01001002


StateBits



Bit 0
// Para1 Valid



Bit 1
// Para2 Valid



Bit 2
// Para3 Valid



Bit 3
// Para4 Valid



Bit 4
// Para5 Valid



Bit 5
// Para6 Valid



Bit 6
// Para7 Valid



Bit 7
// Para8 Valid



Bit 16
// PlantState Ok (1)  / Error (0)



Bit 24
// Curtailment On (1) / Off  (0)

Structure of data for curtailing turbines:


TCurtailCtlData = packed record



MsgType
: LongWord;
// Curtailment TAC



MsgVersion
: BYTE;
// 1



LiveCounter
: Word;



IDNo
: String[10];



State
: LongWord;
// free



Mode
: LongWord;
// Free



Command
: LongWord;
// Curtailment



Data
: array[0..127] of Byte;


end;

MsgType = $01001003;

Data =
Bit weighted specifying if turbine is curtailed. (Bit on = turbine curtailed)


8 turbines per byte, 32 bytes to control 256 turbines.


Remaining 95 bytes spare.

Byte =
x
x
x
x
x
x
x
x


|
|
|
|
|
|
|
|


|
|
|
|
|
|
| 
Turbine-1


|
|
|
|
|
|
 Turbine-2


|
|
|
|
|
 Turbine-3


|
|
|
|
 Turbine-4


|
|
|
 Turbine-5


|
|
 Turbine-6


|
 Turbine-7


 
Turbine-8

Curtailment Service Program

TrbCurtailSvc /Install
( Installs the curtailment service

TrbCurtailSvc /Uninstall
( Un-installs the curtailment service

DcomCnfg


( Configure the service security



Page 17

