[image: image1.png]Enron Wind



CONFIDENTIAL
Proprietary Information









DO NOT COPY  without

written   consent   from

Enron Wind

FIELD ACTION REQUEST

[image: image2.png]Enron Wind





Originator:

Date / Time:

Site / Row / Pad #:

Return FAX #:

Return Phone #:
Matt Allsup


5/30/02             1400


Desert Sky / Curtailment PC


(915) 652-8634


(915) 652-8650 /  638-3125

Section B: To be completed by the originator.

CONDITION

 The curtailment computer installed by Joe Chapman controls the turbines based on 10 minute average data and real-time data.  By contract, we have 10 minutes to respond to a City Public Service curtailment request.  Depending on the time of day we start a curtailment, the program can take up 10 minutes to respond to a request.  If it takes this long and it does not shut down turbines fast enough, we could incur penalties from CPS (by contract).

The biggest problem with the 10 minute average is that when a curtailment is officially lifted (when our SCADA operator or, in the near future, a CPS operator clicks the End Curtailment key) the program can take up to 10 minutes to respond.  Since the curtailment is officially over, AEP is no longer getting paid for curtailed production OR PTC’s.  We are curtailed almost every time we can produce more than 70 MW.  That means that usually half the site is shut down.  If the turbines are started on paper, but not producing until minutes later, neither us or AEP can capture that lost production.

These large chunks of time, daily, for a whole month will be a huge amount of lost income for AEP. 

LIST ATTACHMENTS:

REQUESTED ACTION: 

Rewrite the software so it responds in real time.  

EW Part #:

Vendor:


Originator’s Signature:
Matt Allsup









Field Action Request
Section C: To be completed by Project Coordinator.

Reference Number:     _______________        

INITIAL RESPONSE: 



Project Coordinator:

Date:

Time:


Forwarded to:
( Engineering  (Quality     ( Manufacturing     ( Field Op. Group ______________

Section D: To be completed by Originator and faxed back to Project Coordinator after receipt of the FARR.

Are you satisfied with the FARR?
( Yes, I am satisfied.     ( No, I am not satisfied for the following reasons.
List of Reason(s): 



Originator:

Date:

Time:


Section A:





 X  URGENT  	          ROUTINE





FAX to:  (661)  823 - 6466




















_1021801698.unknown

