Confidential and Proprietary


4.0
Environmental Questions
Comments

4.1
Please provide emission profiles with and without evaporative cooling, at load ranges of 0 – 100% (in 5% increments) at ambient temperatures of –15, -5, 5, 15, 25, 35, 45, 55, 65, 75, 85, and 95 degrees F, that include the #/hr and ppmvd of NOx CO, SO2, VOC, and particulates, as adjusted for site elevation.  Emission profiles should also include output, heat rate, exhaust flow, exhaust temp.
Please note that Appendix B-1 of the air permit application provides emission profiles for 75% and 100% load factors at 0, 27, 57, 89, and 95 degrees.

4.2
Please provide copy of emissions compliance testing conducted in accordance with NSPS and Permit to Construct and any emissions testing to validate equipment warranties.
A copy of the Performance Test Report conducted by McHale & Associates prior to commissioning the turbines has been placed in the data room. Due to economic reasons, the EPA accepted this report as conditional demonstration of compliance with NSPS Subpart GG, pending a complete NSPS compliance demonstration to be conducted by January 30, 2001 during CEMS certification.

4.3
Please provide copy of plant monitoring data for fuel nitrogen and sulfur content.
The plant has not sampled for fuel nitrogen and sulfur content in natural gas. The plant relied on sampling data generated by the natural gas supplier to ensure compliance with the NSPS requirements. The plant also has an approval from the EPA to conduct sulfur sampling on a semi-annual basis. 

4.4
Please provide water-to-fuel ratio data during all operating hours.
To be provided by Chris Norris

4.5
Please provide copy of Title 5 application submitted to IDEM.
The Title V application has not been submitted. The due date for this application is April 2001

4.6
Please provide copy of Phase II Acid Rain Application
A copy of this application will be placed in the data room

4.7
Please provide results of CEM certification.
The CEMS have not been certified. The EPA has approved an extension of the deadline until January 30, 2001

4.8
Please provide explanation of stack gas stratification issues.
While attempting to certify the CEMS on August 7, 2000 within 90 days from commencement of commercial operation, we conducted a stratification check on units 1 and 2. One probe location on the edge of the stack indicated high oxygen and low CO and NOx readings. A copy of the stratification emissions report has been placed in the data room. An investigation of the stratification problem has not yet been conducted. The EPA, however, has given an approval to delay the CEMS certification until January 30, 2001, and of a procedure to certify the CEMS despite stratification.

4.9
Please provide NOx, CO2 and CO CEM reports for all operating hours, including ppm, #/hr, #/mmBtu and cumulative TPY.
To be provided by Chris Norris

4.10
Please provide copy of CEM Standard Operating Procedures and QA/QC manual.
To be provided by Chris Norris

4.11
Please provide information on initiation of water injection after startup (i.e. when water injection can be safely initiated).
To be provided by Chris Norris

4.12
Please provide copy of Preventive Maintenance Plan
To be provided by Chris Norris

4.13
Please provide copy of Compliance Response Plan
To be provided by Chris Norris

4.14
Please provide copy of SPCC Plan
The SPCC plan is still in development. The anticipated completion date is November 30, 2000

4.15
Please provide copy of Affidavit of Construction
To be provided by Dave Kellermeyer

4.16
Please provide copy of Operation Permit Validation letter.
The title V permit application has not been submitted

4.17
Please provide explanation of revision to the Permit to Construct dated 3-13-00.
This revision was to incorporate an emergency generator into the permit.

4.18
Please provide potable water supply agreement.
Chris Norris

4.19
Please provide any data on local water supplies, including well logs of local wells.
Chris Norris

4.20
Please provide copies of any Phase II environmental assessments conducted on any properties included in this transaction.
No Phase II assessments have been performed for any of the sites.

4.21
Please provide detail on any zoning restrictions related to stack height or noise.
Dave, Chris

4.22
Please provide water quality analyses of water withdrawn from lake.
To be provided by Chris

4.23
Please provide copy of water quality control procedures, including methods for pH and conductivity adjustments.
Dave, Chris, Norris Harrington

4.24
Please provide explanation of raw water filtering requirements, prior to demineralization.
Dave, Chris, Norris Harrington

4.25
Please provide copy of custom schedule request to USEPA.
A copy has been placed in the data room

4.26
Please provide costs associated with operation and maintenance of CEMs including annual RATA testing, calibration gases, spare parts, etc.
Clean Air Engineering is retained under contract to conduct quarterly linearity checks and annual RATA’s. A copy of this contract has been placed in the data room. There has not been enough run time to obtain an accurate cost assessment

4.27
Please provide copy of contract with Ecolochem for demineralization of water.
Chris Norris

4.28
Please provide copy of CEM warranty agreement with CISCO.
Chris Norris

4.29
Please provide determination of SARA reporting requirements under 311 and 312.
It is our assessment that we do not hold any SARA chemical in quantities greater than 10,000 lbs. SARA reporting is not required. Additionally, this plant began operation in April 2000. The first SARA report, if applicable, is not due until July 1, 2001.

4.30
Please provide explanation of need for a mercaptan  odorizing station.
Chris

4.31
Please provide copies of any hydrologic studies performed at the associated properties.
Chris

4.32
Please provide schedule of all environmental, health and safety required training and associated procedures.
An environmental compliance matrix and a calendar for this site have been placed in the data room

4.33
Please provide maximum water withdrawal rates from the lake reservoir and explain any limitations.
Chris

4.34
Please provide the attachments to Section 3 of the Monitoring Plan, including the natural gas sulfur content documentation and flue flow meter documentation.
Chris – please provide copies of the fuel flow meters maufacturer’s certifications and check to see if we had conducted sulfur sampling in support of the monitoring plan. 

With the delay in CEMs certification until January 30, 2001, we have until December 15, 2000 to submit a revised monitoring plan with the appropriate attachements

4.35
Please provide information of the CO CEM system, including equipment and calculation method.
Chris to provide copy of the CO CEMS Quality Assurance Plan from CISCO

Status Legend:  A = Actual date received, P = Partial Response Received

DPL-Wheatland-env
10/20/00
- 3 -


