[image: image1.png]


[image: image2.wmf]Highly Confidential

Commercial Nuclear Power Plant Monitoring

[image: image3.png]



Weekly Monitoring Report For Requested Commercial Nuclear Power Plants

12/6/00 – 12/13/00


Report #:  WE001213

[image: image4.wmf]       = MidWest (ECAR, MAIN, MAPP) 

       = South (ERCOT, FRCC, SERC, SPP)      

       = New England (MAAC, NPCC)

	
	
	Unit
	Update on 12/13/00
	Projected Status
	Our Opinion

	111
	
	Beaver Valley 2
	0% power in forced outage
	Restart expected on 12/17/00
	The licensee is attempting to repair the leak but is not certain of when the leak will be controlled allowing the unit to restart.  Current estimates are that restart should commence sometime this weekend.  That estimate is consistent (perhaps a little lengthy) with historical RCS leaks in containment.  We will continue to monitor the situation and inform you of more definitive estimates as work proceeds.

	112
	
	Cook 1
	0% power, in regulatory outage
	Restart expected on 12/16/00
	Cook 1 has progressed through Mode 4 hot shutdown (entered on 12/7/00) and into Mode 3 hot standby (entered on 12/13/00).  This advance is consistent with expectations for a 12/16/00 restart of the unit.  Power ascension after the restart should be conservatively slow to ensure function of all systems.  Possible delays and/or shutdowns may occur due to leaking systems that have not operated for some time.  Full power, however, is expected to be reached by 12/26/00.  

	113
	
	Perry
	95% power in coastdown to refueling
	Next refueling outage expected to begin on 2/17/01
	Perry continues to report a coastdown to their refueling outage.  It should be a long, slow coastdown since the refueling outage start date continues to be affirmed as 2/17/01.

	121
	
	Kewaunee
	96% maximum power 
	Next RFO expected to start on 10/13/01 
	Kewaunee continues to operate fairly consistently at the 96% power level.  We expect continued performance at this level unless significant steam generator leaks occur.  The risk with this unit is not as much for derates or short term forced outages as it is for a steam generator tube problem forcing a long term outage.  No indications currently exist that the risk is any more elevated than it had been for the past few months.  

	122
	
	Point Beach 2
	0% power in refueling outage
	Restart expected on 12/16/00 
	Point Beach 2 has advanced once again to hot shutdown after completing some minor maintenance.  We expect restart to occur by sometime this weekend, 12/16/00-12/17/00.  The unit has operated well over the past couple of years, and we expect a capacity factor of about 96-97% over the coming cycle.

	131
	
	Prairie Island 1
	0% power in forced outage 
	Restart expected on 12/14/00
	Prairie Island 1 has completed maintenance on a reactor coolant pump.  The unit is moving toward restart, and we expect that to occur by 12/14/00.  The maintenance outage should not affect the start of the refueling which is scheduled for 1/20/01.  The unit has performed very well over the past couple of years.

	231
	
	Oconee 1
	0% power in refueling outage
	Restart expected 1/7/01
	Oconee 1 continues in a defueled condition in the middle of their refueling outage.   No significant problems have occurred so far that would jeopardize the 1/7/01 restart date.

	232
	
	Summer
	0% power in refueling outage
	Restart expected 1/11/01
	Restart of the unit has moved out to mid January 2001 (1/12/01-1/15/01).  Site personnel continue to report slow but consistent progress in the welding of the replacement pipe.   The possibility continues to exist that improvement in the timing of the welding could improve the targeted restart date.  

	241
	
	ANO 2
	45% power, in power ascension following refueling/steam generator replacement outage
	Full power expected on 12/17/00
	The turbine testing has completed and the unit synchronized with the grid.  ANO 2 is in the process of power ascension and should reach full power by the end of the week.  ANO 2 is an average performing plant.  We expect a capacity factor in the low 90s over the coming cycle.

	321
	
	FitzPatrick 
	55% power
	Full power expected on 12/14/00
	The unit is struggling with the repair of a feedwater pump which it is performing while the unit is online.  The removal of the feedwater pump from service, however, has required the unit to derate to about 55% power while the repairs are being made.  Completion of the repair and return to full power should occur soon within the next day or two.

	322
	
	Indian Point 2
	0% power, shutdown in a refueling/steam generator replacement outage
	Restart expected on 12/11/00
	The licensee has made progress toward completing the Indian Point 2 outage.  The unit has moved to hot shutdown and is expected to restart by 12/17/00.  Full power should then be reached by 12/22/00 or 12/23/00.

	323
	
	Seabrook
	0% power, in refueling outage
	Restart expected on 12/30/00


	Seabrook continues work on its emergency diesel generator.  As reported earlier, the significant factor as to whether the outage will complete by the end of this month, or if it will continue for several (3-5) more weeks is whether the crankshaft will require significant rework or replacement.  We will report to you when that determination is made.


LEGEND:

RFO – Refueling Outage

FO – Forced Outage
E:\Task 3 - Monitoring\Weekly Rpt\East Summary 001213.doc

_963987986

_963988101.unknown

