EXHIBIT A

ELECTRIC MOTOR DRIVER (Gallup Station)

DESCRIPTION OF ASSETS


ELECTRIC MOTOR - A 10,000 HP, 1.20 SF (rated 12,000 HP with service factor), 1500 RPM, 4160 VAC, 6( (dual winding).  The motor is externally ducted enclosure rated for operation in a Class 1, Group C & D, Division 2 environment.  


VARIABLE FREQUENCY DRIVE (VFD) - The VFD is a 12/12 pulse load commutated inverter, 4160 VAC, 6(, liquid cooled. VFD includes Isolation transformer, Source converters, DC link reactors, Load inverter, VFD control panel, Filter capacitors, Termination cabinet, Liquid heat exchanger system (closed system), and Power Factor Correction Capacitors

HIGH SPEED GEAR - The high speed gear is a single stage, parallel shaft, horizontal offset speed increaser to match the specified electric motor at 1500 RPM to the centrifugal compressor.  All shafts are supported with split sleeve babbitt bearings.


HIGH VOLTAGE SUBSTATION - Designed for a 115 KV primary supply.   The substation will includes dead end structure, two line 115 KV Switcher, 12 MVA primary transformer, low side service metering, and 8 KV switchgear


HARMONIC FILTER - A harmonic filter is provided within the substation.  


