[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Sat., Jan. 26, 2002  (Armitage, Munson, Welsh, Cummings)

	0940
	
	El Paso’s timer is on me for high water.  I’ve had people at LaPlata most of the morning.  I’ve got Bloomfield out hunting.  He’s going to hit the El Paso runs first just to make sure it really is wet and it’s not their water meter and then start down the line.  Hopefully within and hour we’ll have it taken care of.

Cummings



	1005
	Hugoton
	We’re showing an on/off alarm on H2S at Hugoton.  The H2S climbs to about 1.8, drops back down immediately and then spikes up again.  I spoke with Denny at Hugoton about this problem.  He said to disregard.  He said they are having a problem with the tape on the monitor.  Hopefully it will be looked at get fixed next week when his technician gets back.  He assured me that there is not any H2S problem at Hugoton.

Munson



	1040
	Finney 3
	We’re showing some high moisture at the Finney 3 location.  I notified Randy on the Finney team.  He said that either or one of his teammates would take care of it.

Munson



	1045
	
	Moisture problem in the San Juan later turned out to be the water monitor at El Paso had malfunctioned.  It has been recalibrated and we’re back in business.

Cummings



	1140
	Martin Co. 1
	Unit 5 is down.  Gary checked in from that team and said that either he or another team member would take care of that.

Munson



	1207
	TW Beaver
	We’re getting some high moisture readings again.  It looks like it came down through the night.  About 9:00 this morning it started rising and it’s about 7#.  We got a hold of one of the pipeline people and he was going to call somebody that looks at the Ivanhoe dehy and see if they can take another look at it and get it back down.

Welsh



	1240
	Finney 3
	Rick checked in from Finney 3.  He has taken care of the moisture problem.  He has dropped the moisture down to around 4#.  It’s still seems to be coming down.  He said that he believed the problem was caused by high discharge temperature gas.  He was able to change some of the louver settings on the unit which would lower the gas temperature.  I passed on to him that we all seem to be having a moisture problem at Finney 2 and Finney 4.  He is going to pass it on to Randy.  One of them will take care of it.

Munson



	1530
	Cunningham
	We asked Crabb to turn Cunningham around for injection status and start injecting with an order of approx. 150, that would be two units.

Munson



	1550
	Clifton
	We requested Mike from Clifton to go out and drop the #30 unit off line due to low spread.  We asked him to split the “C” and “D” lines out at the time that he does this.

Munson



	1550
	Texas Co. 1
	We show an H2S analyzer malfunction.  I notified Joy.

Munson



	1603
	Clifton
	Unit #30 is down as requested.  I notified Dan at Bushton.

Munson



	1705
	Texas Co. 2
	Units 6 and 3 are down.  Dee is going to take care of it.

Munson




1830 to 0630 Shift Sat., Jan. 26, 2002  (Hardy, Henley, Spain, Monden)

	1843
	Station 2
	Unit 202 just went down. Stacey is going to go out and check it out for us.

Henley



	1900
	Shell Tippet
	Their control room called us.  Ed talked to them.  They said that they would be making the delivery to Oasis all night and wouldn’t be able to turn back around and catch up on the gas they need to deliver to us.  Passed this on to Harry Woodson.  He’s going to make some calls and call me back.

Hardy



	1859
	Bloomfield
	High pressure suction just jumped up.  I have one of the Bloomfield guys on call going out to check it out.

Henley



	1930
	Bloomfield
	The electric unit was down.  It never did flag as being down.  The processor went out and that’s why it never did flag as being down.  He’s out there now and is going to put it back on line.  I did talk with WFS and they are aware of our problem.

Henley



	1955
	Texas Co. 2
	Dee just called in.  He said he has the units back on at Texas Co. 2.  He is going to leave 2, 3 and 6 on tonight and take 1 down.

Spain



	2000
	Meade TBS
	Jay called from Meade.  We were getting a high delivery pressure alarm there, about 257#.  We’ve got a high/high of 245.  Jay went out earlier and is cutting back on the cut-off to the TBS.  He lowered the regulator a little.

Spain



	2030
	Cunningham
	I gave Linda an order to increase the injection rate from 150 to a 250.

Spain



	2015
	Bloomfield
	Have the electric back on line.  Everything is looking a lot better.  I notified WFS.  We’re increasing Milagro to common in on rate.  Also called the Gallup team, spoke with Dean.  During this mess with losing the electric at Bloomfield, Gallup went into surge.  The unit stayed on line but it does have an alarm.  Dean is going to go look at it as soon as things line out.

Henley



	2140
	Minnegasco
	McCray with that company called in and said that he wanted to increase his injection rate up by 20 million.  They had already increased their injection rate to Glenwood by 60 earlier today and he wanted to do another 20 on top of that.  That brings that up to an 80 million injection at Glenwood.  I called NGPL that takes care of Glenwood, spoke with Juan.  He said he did receive a call from McCray and we could go ahead and start increasing the injection flow.

Monden



	2235
	Shell Tippet
	The operator called.  They’ve got our flow rate back up.  They decided not to try to make their other delivery to Oasis.

Hardy



	0045
	Texas Co. 1
	Unit #2 went down.  Dee Chapman is going out for us.

Spain



	0034
	Bloomfield
	The electric went down again.  Brian went out there.  He did have to change the processor out.  He is just now leaving the station and it’s now 0215.

Henley



	0128
	Station 2
	Unit 2 is on line.

Henley



	0215
	Aquila
	Talked to Chad.  They’ve got their turbine back up and running, delivering.  Talked to Ken also over at Roger Mills who is going to go out and open up the line to make a delivery to ONG to keep from pressuring Aquila out.  Their push will help us deliver to ONG also.

Hardy



	0300
	Texas Co. 1
	Dee just called back in.  They had an ESD out at the station.  The power gas froze off and the station ESD’d.  He’s got some help coming out.  They’re going to put some methanol in the line and get it thawed out.

Spain



	0305
	Stevens Co. 2
	Unit #9 went down. About 0330 I got a hold of the on call person Bruce.  He is going to go out for us.

Spain



	0525
	Stevens Co. 2
	Bruce called in.  He’s got unit #9 back on line.  He had to change the sparkplugs in it.

Spain




slb  

