[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Fri., Dec. 28, 2001  ()

	0939
	Texas 2
	Just got a call from Dee.  They shut units 4 and 5 down because they’ve got 6 back available and they’ve got it on now.

Hall



	0710
	
	Got a call from Jim Merrick.  He said they are going out to do a test on Chatfield compressor station.  They were going to lower the LaCrosse take-off from about 710 down to 670#.  That way they can start the unit at Chatfield and run their tests.

Calhoun



	0815
	Hubbard
	Put the unit on line.  That was due to a test that was scheduled with Corn Belt and Alliance.

Calhoun



	0815
	Faribault
	Had Jim VonRuden put the unit on line.  We were dropping off going west towards Willmar out of Farmington and also the “BC” was starting to fall.

Calhoun



	0855
	Grundy Center
	They were doing 58 million out there.  As we had to put Hubbard on to do the test I went ahead and took them to a zero flow rate. Also our totals from NBPL were being cut today by almost 75-80 million so we went ahead and made that change there.

Calhoun



	1005
	Hubbard
	The test with Corn Belt and Alliance was over with.  They turned the unit back over to us to run as needed.

Calhoun



	1245
	Mullinville
	Called and talked to Brian to let him know that Beaver had ESD’d.  Don’t know for sure how long they will be down.

Hall



	1240
	
	Beaver station called and said they just had an ESD.  At 1244 we called Pampa and told them.  They are not at the station at Pampa but they said that it should idle back down.  If it goes down they will go put it back on.  I told them I would keep them posted on that.  We haven’t heard what Beaver’s problem is but they will keep us abreast of the problem.

Welsh



	1200
	NBPL Ventura
	Cut their flow rate from 915 down to 870.  That’s for the new gas day nom.

Calhoun



	1205
	Beatrice
	They are going to put the turbine on the “E” line.

Calhoun



	1200
	Oakland
	Had them put another unit on the “D” line.

Calhoun



	1230
	
	Got a call from Dan Wilson from Corn Belt.  It sounds like there is going to be a peak alert on Hubbard.  They want the unit shut down, that window from about 1645 to 1915.

Calhoun



	1415
	Oakland
	Got a hold of Bob Hall.  We’re going to bring on the “BC” units.

Calhoun



	1330
	Farmington
	They tried their unit #4, put it on.  It went back down.  They said it’s going to be down through the weekend due to they are having to order some parts for the panel board.  Still having ignition and governor problems.

Calhoun



	1350
	Ogden
	Put unit #13 on going north.

Calhoun



	1355
	Farmington
	Put unit #6 on.

Calhoun



	1620
	
	Got a call from Jim Merrick at Chatfield.  They were getting ready to load the unit and put it on line and get some pressure headed back out towards Tomah.  Tomah was down to 508.  Also they were going to go out to the LaCrosse take-off on the “D” line by Owatonna and open that regulator back up and start sending some more gas out towards the Tomah branchline.

Calhoun



	1633
	Hubbard
	Sent a stop command to the unit during the peak alert time frame.

Calhoun



	1629
	ANR Janesville
	They went from 80 million delivery down to zero.  They had lost some units there.  They got them back on at 1649.

Calhoun



	1705
	LaCrescent
	Put a start command in on the unit.  We were down to about 498 at Tomah and it was still falling.  I needed to get that pressure turned around.

Calhoun



	1729
	Sublette
	Just got a call from Steve out there.  He said he’s got a lot of liquids coming in.  That’s what has knocked him down.  He said they may have broke something too.  He’s got water in the fuel on that Haskell Co.  He’s going to try to call Oneok to see if they can do something.

Hall




1830 to 0630 Shift Fri., Dec. 28, 2001  (Hardy, Henley, Monden, Muntz)

	1812
	Clark Co. 2
	Alan called to check the status of the discharge water.  The readings we had from there got as high as about 8.6 today.  He has recalibrated the meter and it’s come down.  We’re at 4.6.  He’s headed home.

Hardy



	1812
	Amoco Abo
	Terry Youngren called in and had me change the high range setting for the differential from 155 up to 250.

Muntz



	1915
	Beaver Co. 3
	Unit 3 is down.  Dennis is on his way.

Hardy



	1915
	Corn Belt
	Called and let them know that I’d be putting the Hubbard station back on line around 7:30.  They said OK.

Henley



	1946
	Hubbard
	The unit is on line.

Henley



	1946
	Beatrice
	Added a 2000 to the “D” line.

Henley



	2050
	Clifton
	Had OCC get a hold of the on call person, Lynn Greenlee.  Asked him to put on the second vertical unit going from “E” to “E” to get more gas going up the “E” line and get closer to the volume that we need to be passing through Clifton.

Monden



	2110
	Mullinville
	Dee called in.  Unit 26 turbine that’s on the “E” to “E” he said it’s low on compressor seal oil.  He has notified his team lead and they are trying to get a barrel of seal oil.  Hopefully they will not have the unit go down.

Monden



	2113
	Sublette
	Unit 23 is back on line.  Steve said that liquid hit the compressor and broke a compressor valve.  That’s the reason that he couldn’t get the unit up and on any sooner.  There are two units running now, 23 an 24.

Monden



	2120
	P3
	Jerry is out at the station.  I had called him earlier and told him that I wasn’t able to get control of the unit with the differential control.  Jerry has put the differential control in manual and raised the setpoint from 170 back up to 250.  He is bypassing gas through the station on a 6” valve recycling at this time.  Trying to get the discharge pressure to stabilize or drop back to 950.  Currently we’re only flowing about 81 on deliveries.  Jerry wants to try to keep the unit on tonight so it will be available when the rates pick up tomorrow.

Muntz



	2144
	Clifton
	Unit 29 is on line at 2125.  Lynn is headed home.

Monden



	2240
	Tescott
	Had OCC get a hold of the contact person.  I spoke with Gary from Tescott.  Asked him for a turbine on the “D” to “D”, shove more gas up to Clifton.  With their new automation he said he would like to be at the site when I put the unit on that service and started it.

Monden



	0005
	Station 1
	Received an AC power fail alarm, station alarm, intrusion alarm and air compressor alarm north and south.  Notified Mike at station 1.  He will go check it out.

Muntz



	0019
	Tescott
	Unit #3 that was going to go on the “D” to “D” got warmed up, it did load up and then the unit went down on high oil differential.  Gary is at the site.

Monden



	0029
	Station 1
	Mike just called in.  He said that he’s on his way out to the station.  They had a power failure and the generator is not running.  He is going to go check it out.

Muntz



	0223
	Tescott
	Gary got the unit on the “D” to “D”, unit 3 on line at 0130.  It has stayed on line since.

Monden



	0244
	Texas Co. 1
	Unit #3 has gone down.  Dee Chapman is going to the site to check it out.

Monden



	0255
	GPM Zia Plant
	Flow rate dropped off from around 31 down to 1.9.  I called the Conoco Maljamar plant and spoke to Tom.  He is going to look into it.

Muntz



	0450
	Mullinville
	Dee the operator called in and said that unit #26 the turbine is down.  It was running “E” to “E”.  He said at this time he does not know what it went down on for sure.  He does have people on the way out to help him get it back on.

Monden



	0500
	Beaver
	Called and talked to Randy.  Told him that they lost a unit on the “DE” at Mullinville.

Hardy



	0522
	Stevens Co. 6
	Unit #4 has gone down.  Steve Benavidez called in.  He is going to go check it out.

Monden



	0523
	Cunningham
	Spoke with Linda and asked her to bring the withdrawal up to 400 due to the fact that the unit at Mullinville had gone down on the “E” line.  It would help supplement some of the gas to the turbines at Macksville and try to help keep those on until they can get the turbine back on at Mullinville.

Monden




slb  

