 [image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Sat., Oct. 20, 2001  (Braswell, Hall, Barry, Ellington)

	0605
	Red Cedar
	Called the OCC for the on call for the LaPlata team.  At the Red Cedar point we’re reading extremely high BTU at about 1575.  The flows are off because of that.  I talked to Red Cedar people and they were reading high noms, volumes as well.  I’ve got Larry going out there to check that out.

Braswell



	0640
	WT2
	Lost unit #2.  Called the OCC for the on call.  Touched base with Benny Lopez out there.  They’re leaving #2 down and putting #3 unit on and see how that works.

Braswell



	1030
	Hugoton
	I’m showing #1 unit down.  Called the OCC and requested the on call.

Barry



	1110
	Sublette
	Unit #20 down.  Called the OCC and requested the on call.

Barry



	1225
	Redfield
	I called the OCC and they got a hold of the on call.  Just got a call back from Redfield.  The on call said he’d call Smithson who he thought might be out there.  He is and he’s out there testing.  He’s the one that showed the alarm on the #2 unit.

Hall



	1301
	MidAmerican
	Just called and talked to Dave about Quad Cities.  He has averaged 50.5.  He has dropped his rate back to 48.1 on a spot.  The nom is 19.2 which means that he is over.  He said that he would be truing up with some of the storage and all in the morning, everything at this point.

Hall



	1531
	Redfield
	Called the OCC.  They got a hold of Ron the on call.  I told him I thought the fellow had already left out at Redfield but he said he thought he was still there doing some other things.  I told him we showed #4 to go down.  The volume has dropped so he’s going to call out there to see for sure if the guy is still out there. If he’s not Ron is going to run out there for us.

Hall



	1544
	Redfield
	Just got a call from Tom.  He’s still out there.  He’s putting the #4 unit back on.

Hall



	1620
	Pierz
	Called the OCC.  They got a hold of the on call.  He said he’d have to get a hold of Mark and see if he can go to the Willmar office.  Got a problem with a discharge sensor out there because the unit went down and the pressure was only 812, suction of 718.  With this problem they’ve got to kind of trick it to get it to come on and they’ve got to be at the Willmar office in order to get it down.

Hall



	1640
	Pierz
	Got a call from Mark.  He got Pierz going again.  I called Terry at Viking.  He’s going to also possibly shift some of it over to Polk.  We’ll take 5 at Pierz and 5 Polk.

Hall



	1700
	Meridian
	Mary called from Valverde point and said that they have two trains that were down.  They do have people out there already trying to put those stations back on.  In the meantime they will at least try to keep us at a rate of at least 100 million until they can get back on.  Otherwise if they drop below 100 million they will have El Paso cut some more gas.

Braswell

 

	1728
	Sandstone
	Sandstone is finally up to 23 million.  They’ve been slowly coming up all day.  We put two units on earlier at Roger Mills.  Had Jerry go out and do that.  Our flow rate is where it needs to be however we’ve lost the Custer Co. delivery point.  It was doing about 16 million.  Jerry tells me that we can’t do both points.  He went ahead and put he unit on that we needed to make Sandstone because Sandstone had called about three times today asking about it.  We had our units on and the valve was 100% open but they still weren’t flowing.  I reported that to their gas control.  They sent someone out and it started flowing.  They evidently had a valve closed on their side.  They never did call and let me know what they found.  Once again, Sandstone is flowing for the 24 million.  We have lost Custer Co.

Ellington



	1736
	
	Called the OCC for the on call for Atoka 3.  Unit 842 is down.

Braswell




1830 to 0630 Shift Sat., Oct. 20, 2001  (Alvarado, Moore, Coash, Cochran)

	1800
	WT2
	It looks like unit 3 is down.  I made a call out and talked to Mike.  Let him know that my suction pressure has come up about 10# and my flow has dropped off 100.  I’m still showing RPM’s on both units but I’m pretty sure it’s 3 that is down. They’ve been having problems with, here we go again.  He’s headed out.

Moore



	1835
	WT2
	I just received that alarms in here.  Both units are down.

Moore



	1930
	WT2
	Have both units 1 and 3 back on line.  Mike and Benny are going to the house.

Moore



	2033
	Meridian
	Received a call from Sean.  He let me know that I’m going to see a spike on the CO2.  He said that he opened up his bypass some and apparently went too far.  During our conversation I did see it come up to 2.6.  I told him it was way too high.  He said he’s already cut it back so we should see it come right back down.

Moore



	2043
	Meridian
	CO2 is now down to 2.07.

Moore



	2046
	Meridian
	CO2 has now come down to 1.22.

Moore



	2100
	Oakland
	Dropped one unit.  We had three units on there. I’m trying to build some pressure back in towards Glenwood because we’re pressured out there.  Trying to get that flow back up.

Cochran



	2100
	Palmyra
	Got a hold of personnel there.  It looks like the “E” to the “D” block valve has come open. They are going to go back out and close that also so we can try to build some pressure up towards Glenwood, get them on rate.

Cochran



	2212
	Station 2
	We took unit 2 down there, no demand.

Moore



	2235
	Sublette
	Received a high level alarm on their condensate tank.  I contacted OCC and got a hold of the on call person.  I spoke with Russell Stewart.  I advised him that this alarm had come in.  He said they’ve got the tank indicating about ¾ full.  He will have somebody pick up the liquids off of it in the morning.  He indicated it was about a 400 barrel tank.

Alvarado



	2307
	Station 1
	Unit 1 – I received an alarm here on it.  That unit has not been running for the past few days but Mike is going to go out and check.

Moore



	2330
	Station 1
	Received a call back from Mike.  He went out and checked the station. He said there is not any problems there.  It looks like it was a late alarm for the unit shut down which happened a few days ago.

Moore



	0051
	Morton Co. 1
	Received an H2S analyzer malfunction.  I’ve contacted OCC and spoke with Bill.  He advised me that he would take care of it first thing in the morning.  He seems to think that maybe the electricity went off and the machine is not resetting.

Alvarado



	0110
	Meridian
	The CO2 has come up again to 2.06.  Made a call over there and talked to Sean.  He said that he’s already cut some of the bypass gas again.  He is having problems with one of his trains but he was trying to get it under control.

Moore



	0124
	Meridian
	The CO2 is back down to 1.13.

Moore



	0320
	Oasis
	Received a call from Bruce.  He said that they are having some pressure problems and he would like to cut back about 10 that he’s taking from us for possibly a couple of hours.  I told him we could try and see what it does but please take his gas as soon as he’s able.

Moore




slb  


