[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Wed., March 20, 2002  (Barry, Hall, Armitage, Muntz)

	0600
	
	Randy is out at WT1 starting the #2 unit, getting it ready to come on line.  This morning we do have a total shutdown outage at WT2 station.  At this time we’re going to utilize the time between about 6:30 and 9:00 to build the pressure up to try to maintain and keep our deliveries stable south of WT2.

Barry



	0700
	
	This morning with the outage at WT2 the 24” line south of WT2 we have a scheduled volume from NGPL Winkler of 50 million.  What I’m going to do is at Halley we’re going to set Halley up coming from the 24” from TW going to the 24” NNG.  We’ll take the gas from NGPL and just move it over to Halley as we do have that gas scheduled today.

Barry



	0820
	Cunningham
	They are in the process of taking the electrics down and leaving two dual fuels running at Cunningham.  The flows will drop off until they get all of their electrical work done and then they will come back on line back to withdrawals.

Armitage



	0830
	WT2
	At this time we commoned up the 30” north and south.

Barry



	0925
	Oakland
	Called the OCC.  They got a hold of the on call.  Asked him to put another unit on the “D” line there.  Also called and asked him for the on call for Palmyra.  Got a hold of Dale and he’s going to put another one on at Palmyra on the high side also.  Just keep the gas moving up towards Ogden, get their suction back up a little bit.

Hall



	0955
	Coyanosa
	Rick called and said that he has the Coyanosa regulator repaired.  He requested I put a 900 setpoint in it.

Muntz



	1322
	Amoco LaPlata
	I called the Floreda plant.  Right now we’re running short of our schedule of 160.48, current spot is 152 and we’re only averaging 154.  I spoke with Nester.  He said he was working on trying to get some more gas coming our way.

Barry



	1320
	Cunningham
	They’re on the way back up to full capacity of 225-230.

Armitage



	1410
	Hubbard
	Lost Hubbard so I called the OCC.  They got a hold of the on call.  He looked the alarms and everything and was able to clear them.  He said there was just a blip in the power to it.  I gave it a start command.  It is coming up on line.

Hall



	1438
	
	Ken called from Griffith Energy.  He said that the start up date would be Friday instead of this Thursday.

Barry



	1445
	
	Dennis with El Paso called in.  He informed us that in the Gallup area they would be doing some work tomorrow and they would be venting some gas to the atmosphere so if we happen to have any kind of phone calls reporting gas in the atmosphere they are working on their line.

Barry



	1523
	ONG 3
	Just sent a zero to ONG 3.  We have accumed the nom rate for today.  It shows that we have accumed 7.0 on a 6.5 nom.

Muntz




1830 to 0630 Shift Wed., March 20, 2002  (Moore, Alvarado, Barnes, Cochran, Coash)

	1805
	LaPlata
	Received an alarm in here.  The discharge pressure jumped up to 1046# which has got to be a bad read.  The units are on.  It did drop back down to 1011 in about 5 minutes.  I talked to David the on call.  He’s going to run out and check it.  During our conversation it got back down to 1001#.  I did receive a station alarm.  He’s going to go out.

Moore



	1818
	Stevens Co. 2
	AC power failure – The station is down, no flow.  Mike Zielke called in.  I advised him that all of the units that were on, 6, 7, 8, 9, 10 and 11 are down.  Unit 3 was not on.

Barnes



	1828
	Hugoton
	Unit 5 and unit 3 down.  I advised Danny.

Barnes



	1901
	Hugoton
	Unit 4 down.

Barnes



	1910
	LaPlata
	The discharge jumped up to 1018# again.  It’s bouncing around.  I got a hold of David again.  He is back on site there.  I think he’s called someone else out.  They are going to check that unit out and see what’s causing that pressure to jump around like that.

Moore



	1918
	Stevens Co. 2
	AC power back on, alarm cleared.

Barnes



	1923
	Hugoton
	Units 3, 4 and 5 on line.

Barnes



	1948
	Stevens Co. 2
	Units 6, 7, 8 and 9 back on.

Barnes



	2018
	Hugoton
	Unit 3 back on.

Barnes



	2018
	Stevens Co. 2
	Units 10 and 11 back on.

Barnes



	1930
	Monument
	I received an alarm on unit 1.  The units are down.  I got a hold of Randy and talked to him about it.  He’s going to make a call.  He said he may go out but he’s going to talk to someone about it because it may be able to wait until morning.  He’ll let me know.

Moore



	1933
	Dagger Draw
	Received a call from John out there.  He let me know that our valve shut and we lost flow which that did happen.  I made a call out and talked to Carl on the Artesia team.  We did lose Atoka 3 after that.  Carl has made it to Atoka 3 and Terry is headed to Dagger Draw.

Moore



	2044
	Dagger Draw
	It is flowing again.  At Atoka 3, unit 761 is back on line.

Moore



	2034
	Stevens Co. 2
	Units 6 and 9 down again.

Barnes



	2047
	Stevens Co. 2
	Units 6 and 9 back on.

Barnes



	2124
	LaPlata
	Received a call from David.  He let me know that they rescaled the transmitter there and they pulled a lightning transmitter.  He said right now everything is running pretty steady.  We are hitting right at 1008 on discharge but he said it’s running steady.  It looks like everything is OK at the time and to give him a call if we have anymore problems.  He doesn’t believe that we were actually getting 1040 or 1016 discharge pressures that were coming in here earlier.  He said through the night as it cools off the discharge should come down as things speed up.

Moore



	2125
	PNM Rio Puerco
	We are flowing at that point finally.  At this time we need to be doing about 60 there to make rate for the day.  We are doing about 52 and it’s coming up.

Moore



	2200
	PNM Rio Puerco
	We lost flow there again.  With their big unit on they were sending up 100 million, it jumped up.  Our valve ended up shutting in again so I’ve got OCC trying to get a hold of someone to get them to go back out and get this valve opened back up.  I’m not having any luck here.

Moore



	0137
	Meridian
	I called there and talked to Mary.  The CO2 has come up to 2.1.  She is going to cut some gas.

Moore



	0053
	Sublette
	Unit 23 down.  Steve the on call operator called in to confirm it and will attempt to restart.

Barnes



	0133
	Stevens Co. 2
	Unit 10 down. Mike is in route to the location.

Barnes



	0150
	Sublette
	Unit 23 is down on low suction pressure from Oneok.  Steve who is out the Sublette station has paged Oneok with no answer.  Unit 23 is now in remote start and we’re waiting for more pressure.

Barnes



	0222
	Sublette
	Haskell field pressure is 157 and unit 23 is on by remote start.

Barnes



	0228
	Stevens Co. 6
	Unit 5 down.  Mike Zielke who is still at Stevens Co. 2 with unit 10 that is down, he said he’ll leave Stevens 6, unit 5 down until morning.  It looks like the volume impact is negligible at this time.

Barnes



	0302
	Station 2
	Unit 10 will remain down due to an electrical start malfunction.  The volume with unit down is 18.5, averaging 19.5 and the nom is 19.

Barnes



	0236
	Ellis Co. 1
	Unit 2 has gone down.  Contacted OCC and spoke with Steve Ridenour.  He is going to be going out to check on this unit.

Alvarado



	0359
	Ellis Co. 1
	Unit #2 is back on.

Alvarado



	0408
	Ellis Co. 1
	Unit 2 has gone back down. Steve Ridenour is turning back around to head back to the station.

Alvarado



	0459
	Ellis Co. 1
	Unit #2 is back on.  Steve said he’s going to hang around the station and make sure that this unit stays on.  He is having some problems with it.

Alvarado




slb


