[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Tues., Feb. 19, 2002  (Barry, Hall, Armitage, Braswell)

	0813
	Belleville
	Called the OCC and they got a hold of the on call for Belleville.  I passed on to him that we’re having a lot of trouble with our scada out there.  It’s coming and going.  We get a good scan about every other one.  Also passed on to him that this morning when we tried to start the #1 unit it didn’t come on line like it was supposed to.

Hall



	1248
	Mound
	Called the OCC.  They finally got a hold of Bob.  He said that he would tell the technician who handles that and see if they could get it fixed.  I told him that our technician had checked it out and that it was giving a busy signal.  He said that the modem is probably hung up on it.

Hall



	1400
	Earlville
	Called the OCC.  They got a hold of Ronnie.  I let him know that I had a DC battery charger failure alarm.  He said that was probably caused from the generator alarm I had this morning.  He said the generator alarm was probably because the generator was due to run, it kicks off early in the morning occasionally to make sure that it is still ready to go whenever it is needed.

Hall



	1439
	Ventura
	Called the OCC.  They got a hold of John Tammen.  Asked him about putting HP on the “C” suction at Ventura.  He said he would get a hold of Wayne Kozisek and see if they could get it on.

Hall



	1445
	Ventura
	Called the OCC.  They got a hold of the on call.  They are going to put units on the “C” line at Ventura.  Wayne is going to put three verticals on for us.  Also got a hold of Beatrice through the OCC.  Bob is going to put on the unit there.

Hall



	1530
	Hubbard
	Called the OCC because I lost Hubbard.  They got a hold of Jeff.  I had a call just now from Pierre.  He’s headed over there to Hubbard because he couldn’t get it reset from there.

Hall




 1830 to 0630 Shift Tues., Feb. 19, 2002  (Barnes, Alvarado, Moore, Cochran, Coash)

	2227
	Woodward Co. 3
	Unit 4 is now back on. There was a line freeze which was delaying the restart of the unit.  Bill Foresman says if another unit goes down at Woodward 3 to leave it down until morning.

Barnes



	2249
	Beaver Co. 7
	Unit 4 down.  The operator received the page.  Stan Luck will restart.

Barnes



	2310
	Beaver Co. 7
	Stan Luck called to say that unit 4 will remain down.  They plan to work on this unit in the morning.  He was able to speed up the other units, 1 and 2.

Barnes



	2342
	Plainview
	Station alarm – Advised Ken Yarborough.

Barnes



	0000
	Plainview
	Andrew called in about the station alarm.  He’s pretty sure that it’s a malfunctioned gas sniffer which he will change out tomorrow.  The station alarm will remain in alarm for tonight.

Barnes



	0400
	El Paso Waha
	El Paso agreed to take the 5 scheduled for tomorrow on today rather than shutting in now at a 16 accum.

Barnes



	0425
	Roger Mills
	Unit 2 down and it will stay down, no demand in that the pressure is still high enough to deliver to ONG3.

Barnes



	0441
	Woodward Co. 3
	Unit 4 down and will stay down as previously entered.

Barnes



	0528
	Spearman
	Dehy #3, 9.8# of water.  Advised Gary Flowers.

Barnes




slb  

