 [image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Fri., Oct. 12, 2001  (Monden, Muntz, Hardy, Spain, Henley)

	1049
	Mitchell Ellenberger
	Their nom had gone to zero.  Notified Ken Gray and Al Haney, spoke with them about it so it wouldn’t backflow.  They were already on zero this morning at 9:00.  Al was going to go by there and check and make sure the control valve on gas quality had shut.

Monden



	1130
	Palmyra
	I just spoke to Dale Johns.  Asked him to take the turbine off the “A” line.

Spain



	1151
	Mitchell Ellenberger
	Had a nom of zero for today.  Janet McDaniel called me and told me that their nom had come up to 10 and that Western Gas Midkif, POI 54018, had gone down by 10 to a 38.  Mitchell POI is 89.

Monden



	1152
	Sandstone POI 3482
	Had a nom of zero.  Scott informed me that their nom went up to 20 million delivery to them.  They had a 10 million delivery from yesterday and will add that on to the 20.

Monden



	1312
	Mitchell Ellenberger
	Spoke with Al Haney about the H2S reading.  It seemed to be a little bit too good of a reading.  It was reading .001.  He said they will check it out later this afternoon.

Monden



	1450
	Ogden
	I sent a remote stop to unit #13.  All of my units going east were slowed down.

Spain



	1610
	Palmyra
	Sent a remote stop to unit #23.  I need to reduce the Clifton flow by about 80 million.  Got 900 going through Clifton.  Just need a little over 800.

Spain



	1724
	Seminole
	Door alarm at the station has come in.  Notified OCC for the contact person.

Monden




1830 to 0630 Shift Fri., Oct. 12, 2001  (Braswell, Barry, Hall, Ellington)

	1801
	Jal 
	Received a unit alarm out there.  Called the OCC for the on call.  Kay called in.  She is going to contact Lorenzo who is the other on call person.  He called in and said that he had some hot valves on that unit.  He was taking it down to fixing the valve.  Changing it out will take approx. 45 minutes.

Braswell



	2049
	Woodward Co. 2
	Lost unit #4.  Alan called in.  He received a page.  He said he would take care of it.

Braswell



	2226
	Atoka 3
	Unit 842 is down.  Notified OCC.

Ellington



	2320
	
	McCray with Minnegasco called in.  He said they wanted to increase the injection at Glenwood by 30 million.  He said he would go ahead and fax us the necessary information and also call NGPL.  At this time I also called NGPL and verified the increase with them to make sure that they were aware of what was happening.

Barry



	2344
	Atoka 3
	Unit 842 is back on.

Ellington



	2345
	WT2
	Called Darrel Mason to go out to WT2 and open the 30”.  Been trying to move some gas from WT1 down.  All of our valves are 100% open there.  I spoke with Randy just to make sure that one of the valves hadn’t pinched off.  We’ve had that problem before.  He went out and made a visual inspection and said that everything is 100% open.  We called Darrel to question about the valves at WT2.  He wasn’t sure so I called Mike Curry.  He said that the 30” was closed so we’re pulling strictly on the 24 and it’s going across the 16” bypass.  We are not getting the gas down to WT2 that we need.  Also I called station 9.  Remotely shut unit 3 at station 9 down from gas control.  Jesse is going to have to go out and make some valve changes because we are needing to put 51 million up the Panhandle.  To do that without compression he is going to have to set station 9 up to free flow from the mainline into the Panhandle.

Ellington



	0030
	Norval Pecos
	Got a call from field services.  They informed me that they were getting a little stuffed right now in their lines and that they needed for us to cut back at the Norval Pecos point.  We had been over delivering to them earlier because of the downtime on the Seminole turbine, trying to make up some of that gas from the earlier part of the week.  They were actually taking about 108 million.  We cut them back to about 75 million.  They said everything looks good for tomorrow.  They will pick things back up again tomorrow if everything looks OK.

Braswell



	0030
	Station 9
	Unit 3 is down.  I tried to shut it down from gas control 3-4 times and it wouldn’t happen.  Jesse shut it down manually when he got there.

Ellington



	0156
	Citizens
	The Kingman interconnect heater outlet temperature, I’ve got an alarm of 49.7 degrees.  I notified Bo of the Kingman team.  He will go out and take a look at it.

Ellington



	0222
	Sublette
	Just got a call from the on call there.  He had gotten paged by the #23 unit, it’s down.  He’s headed out there to take care of it.

Hall



	0329
	Sublette
	Just got a call from Frank.  He’s got #23 back on. He said it went down on high scrubber level.  He said he didn’t know for sure whether he knocked anything down on Oneok side but he looks like he’s pulling his suction down to 156# now.

Hall



	0345
	Beaver Plant
	Talked to John. I’m having him to pull on the “KB”.  The “KB” is climbing at this time, about 740#.  I’m going to pull that down to about 675-680.  Right now it’s 712.

Braswell



	0347
	Woodward Co. #2
	Lost unit 4.  Personnel called in.  They received the page with the alarm.  Alan called in and said he will go out there later on this morning and put that unit back on.  Still having some field suction problems out there.

Braswell



	0431
	Morton Co. 6
	Lost #2 unit.  I called the OCC after waiting a little bit to see if I was going to get a call.  Gary is the on call. He said he’d probably wait until it gets daylight and then go out there and take care of it.

Hall



	0355
	Beaver Co. 13
	Unit 1 down.  Jeff Hall called in.  He’s going out to check that out.

Braswell



	0400
	Citizens
	Earlier tonight I had called out on the Kingman Citizens point with a low heater outlet temperature.  I never did see any change out there so I called Bo back and visited with him. He had elected to let that go until this morning.  He said it wasn’t critical.

Ellington




slb  


