[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Sun., Jan. 6, 2002  (Henley, Spain, Monden, Hardy, Muntz)

	0620
	Oasis
	Bruce called and said that they were showing high H2S readings out at Oasis Waha delivery point. We show no H2S readings in here.  The valve has closed in the flow but he’s going to send somebody out to look at it, check it out and open it back up for us.

Hardy



	0649
	TW Beaver
	Talked to Eddie Pool.  Told him about the problem out there with high flow with the valve closed.  He thinks that there was probably just a differential transmitter that froze up.  He’s going to head out there to meet Stan and fix it for us.

Hardy



	0805
	Eagle Interconnect
	Don Soppe called in and said that he had a main sense rotor failure.  It will take about an hour to repair.

Monden



	0905
	Linam Ranch
	The operator called.  They lost an inlet turbine.  Flow rate is down to 24.  It will be down for awhile until they can get it back on he said.

Hardy



	0940
	Mt. Hope TBS
	Steve in OCC called in and said that they had a relief valve opening up at this TBS.  He had notified Dave Batie to get it checked out.

Monden



	1020
	Owatonna
	Put the unit on line.

Monden



	1044
	Ogden
	Stacey called in.  He said they’ve got their auxiliary unit back off and they are back on purchase power.  The power company had to replace a transformer.

Monden



	1100
	Alexandria
	Put the unit on line to help build the pressure out towards Benson.

Monden



	1100
	Eagle
	Don Soppe has completed the work on the interconnect and it is now operating correctly on the measurement.

Monden



	1100
	Clifton
	Added unit 31 on the “E” line.

Henley



	1108
	Mapco Whiting
	Darrel from the South Sioux team called in.  He said that the charging unit is bad at the interconnect.  Tomorrow he will have to put a recording unit on at the interconnect because we probably won’t have live scada coming in until he can get the charger fixed.  Until that time he feels like the battery will hold up until he can get a recording unit on.

Monden



	1118
	Mt. Hope TBS
	Spoke with Steve in OCC about the call we got earlier about the relief.  He said he had spoke with Dave Batie and they didn’t have any gas blowing at the time of their arrival but were talking to the lady that called it in.

Monden



	1131
	Mt. Vernon &

Mechanicsville
	Waterloo field team, spoke with Rick Dorsey about low voltages at these interconnects.  He said that they were having Bristol problems on the number of times of polling during the day.  It’s running the battery down on charge capacity which is lowering the voltage.

Monden



	1210
	Guthrie Center
	The unit is on line.

Monden



	1223
	North Branch
	Put unit #3 on in service code 4, cracking west, suction from the south, discharging north.

Monden



	1230
	Farmington
	Got unit #6 on line after trying to start it earlier at 10:42 and not coming on.  About 20-30 minutes tried to start #5 and it didn’t come up on line.  We called the Farmington team.  Scott called back.  He checked it out from his computer and got #6 reset and we’ve got it on line now.

Monden



	1400
	Minnegasco
	Medford Storage – They would like to withdraw 49 million.  I cut back on the regulator at Ventura and brought unit #6 on the “A” line at Farmington pumping to the “BC”.

Monden



	1418
	Terra Chemical
	Scada has gone out, it’s in history.  Had George Margoliner check it out.  He said it was out there at the site.  I’m going to call OCC to get the on call person, it was Clark Matzon.  He is going to Darrel Belt on his team to give me a call about the interconnect.

Monden



	1538
	Terra Chemical
	Darrel called in from the South Sioux team.  He said he was going to have to get a trouble ticket on this.  Will be able to investigate it further with all of the land lines that come in there that polls the information, it just keeps the MTU too busy.

Monden



	1604
	Palmyra
	T-control alarm, shut down alarm – Bob from Palmyra is going to check it out.

Monden



	1638
	Atoka 3
	I just spoke with Armando about the H2S alarm at Atoka 3.  I’m reading 0.163 on station H2S.  It’s trending upward.  Armando is going out to check it out.

Muntz




1830 to 0630 Shift Sun., Jan. 6, 2002  (Barry, Hall, Ellington, Braswell)

	1913
	Oakland
	Called the OCC.  They got a hold of the on call Dana.  He’s going out to put the “D’ line station on for me.

Hall



	1919
	Ogden
	Called the OCC and they got a hold of the on call Stacey.  I asked him about switching 13 from east to north.  With the spread that we’ve got discharge-wise, he said it would be better to shut it off first.  The other reason for the call was I tried putting 17 on and it went down. He’s going to go out and get it on for me, half of it going east and half of it going north.

Hall



	1930
	Faribault
	Called the OCC and they got a hold of Larry the on call.  The reason for the call is I have a lube oil tank temp high/high, 164.7.  When I called it was just a high alarm of 161.  Larry said he would call VonRuden and see if there is anything to really worry about.  Waiting for the call back from Jim.

Hall



	1945
	Faribault
	Just got a call from Jim.  The oil temperature has cooled back down.  He said that the fan takes a little bit sometimes to get caught up with the oil and everything and get it cooled back down once you get the unit going.  It has cooled back down now and looks good.

Hall



	1955
	Pierz
	Called the OCC and they got a hold of the on call Tim.  He’s going to call another guy.  I told him that I had lost Pierz this morning early.  The alarms are not clearing.  With the pressures and all we should be able to free flow with the unit not being on anyhow.  I gave it a setpoint of 10 and no response.  He’s going to call Mitch or one of the other guys and see if they can figure out what’s with it and get it to free flow for us.

Hall



	1900
	
	Called Doug at Cunningham.  Requested him to bring withdrawal of 150.

Barry



	2030
	Willmar
	Just got a call from Mark.  He tried to reset the Pierz location.  He could not get it to respond.  They will go out there first thing and check it out.  He said for some reason it’s not responding, not communicating with his PC and everything.  They will check it out first thing in the morning.

Hall



	2042
	Oakland
	Gave an order to Dana at Oakland for three units to be on the “D” line, for the “D” station to be on.

Hall



	2150
	Beatrice
	Called the OCC.  They got a hold of Ron the on call.  I asked him about which one they would prefer to have started to be added to the “D” line.  He suggested 19.  That was the most recent one on that had been taken off, fairly recent.  I tried it and 19 came right on line.

Hall



	2240
	Waterloo
	Called the OCC.  I was trying to put the station on.  It looks like 1 may be running, 5 started to come on and isn’t, 7 started to come on and it went back down, 8 looks like it is on.  Only two out of the four units that started to come on are on.  Jim is going to go out and take a look at it for us.

Hall



	2240
	Ogden
	Called the OCC because 17 went down.  Stacey is going to go out and put it back on.

Hall



	2245
	Carlton
	Called the OCC.  They got a hold of the on call because it had a station remote alarm, ESD bypass alarm and ESD actuated alarm.  They were only in alarm for one scan and then they turned normal.  He said he might talk to Mike and see what he thinks about it and go from there.  They may check it out tonight or leave it for first thing in the morning.  The unit does seem to be running OK.

Hall



	2300
	
	Called Cunningham and spoke with Doug.  I requested to withdraw 250.  This was an increase of 100 million.

Barry



	2300
	Carlton
	Got a call back from Vern.  He said that since the unit is running fine they will check into that tomorrow morning.  If we should get the alarms again then he will go out and check the printer and see if they are coming in out there as well.

Hall



	2304
	Waterloo
	Just got a call from a fellow out there.  He’s going to see if he can get some of the units going for us.  Told him the main thing was just enough on to pull a good spread for us this morning.

Hall



	2309
	Ogden
	Stacey just called in.  He said 17 went down on crankcase pressure again.  He said that it does that whenever it’s been down for awhile and you first start it up.  He’s got it corrected now and the unit is back on.  He said it shouldn’t go down on that again.  If it goes down again it will be on something else.

Hall



	0230
	
	Received a station H2S alarm at the Oneok Ward point.  Randy called from Oneok soon after I received the alarm. He said that it is probably their H2S monitor. He said instead of calling someone out right now with no more than what they were flowing at this time of about 14 million they will get someone out in the morning to check the monitor out and be sure that it’s working properly.

Braswell



	0328
	Hubbard
	Called the OCC.  They got a hold of Pierre the on call.  Told him I have a substation common alarm at Hubbard.  He said he would go out and check it out for us.

Hall



	0341
	Beatrice
	Got a hold of the OCC.  They got a hold of Beatrice for me.  Ron is going to try putting the two 4’s over on the “E” line and then we’ll put the rest of the 2’s on the “D” line with 19 and 20 and see how that works out for us. Also got a hold of Rodney up at Redfield and gave him a 400 order.  He said it would be a little bit. He’s got to get another fellow out to help him out with it.

Hall



	0406
	Hubbard
	Just got a call from Pierre.  He said he’s about an hour away from the station.  He is going to check out the substation common alarm there.

Hall



	0412
	Beatrice
	Got a call from Ron.  He’s ready to start switching the HP.

Hall



	0420
	Beaver Co. 12
	Unit 4 is down.  Stanley called in to say he is on his way out.

Ellington



	0307
	Stevens Co. 2
	Unit 11 went down.  After speaking with field personnel they said they were going to leave it down tonight.  They had some gas off in the field.  They said it’s down on low suction pressure.

Barry



	0507
	Quad Cities
	I had called for the on call.  They called back in, talked to him as well as Kurt Ritter.  Kurt said that the equipment that is failing out there at Quad Cities belongs to MidAmerican because our check meters are still working.  I just called Bob back with MidAmerican and passed that information on to him.  He’s going to get somebody called out on his side.  I told him if he needed any flow rates or anything later to give us a call because we do still have them and we have the accumulated totals.

Hall



	0505
	Hubbard
	Got a call back from Pierre.  He said it was just a little glitch out there and nothing to really worry about there at Hubbard and everything is fine.

Hall



	
	Tescott
	At about 1:30 this morning I brought on the turbine, unit 5 on the “E” line.  Also after that at Clifton I brought on a recip along with the turbine on the “E” line.

Barry



	0330
	Cunningham
	I issued a new order to increase up to 400.

Barry



	0513
	Waterloo
	Called the OCC.  They got a hold of the on call.  I told him that I just lost #6.  I had lost 5 shortly after he left but I was doing fine as long as 6 was still on. It’s gone down now so I don’t have enough spread on the units.  I’m down to less than 80#.  He will go out and take a look at it and see if he can get us going again.

Hall




slb  

