 [image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Thurs., Oct. 11, 2001  (Moore, Alvarado, Monden, Coash)

	0645
	Valero Spraberry
	Called over there and talked with Randy.  The flow went to zero.  I’m pressured up at Spraberry.  I asked him if they could get their pressure down.  He said they took a unit down, that they are going to put on another because they are doing some testing.  I did inform him that I’m getting close to MAOP and really need him to get the pressure down.  He said they’re working on it.

Moore



	0702
	Bushton Products
	Spoke with Jay.  Made sure they were aware if the ESD that was going on.   He was aware of the ESD to happen at the Bushton station.  They said they were doubled up on their crew at the Products plant to help if any mishaps do occur.

Monden



	0741
	Tescott
	Called in and said they are going to have their UV in bypass for awhile.  

Monden



	0650
	Jal
	Unit 1 down.  Talked with Lorenzo.  They are going to go get that back up.

Moore



	0715
	El Paso
	I called out there and talked to Brian.  Asked them if they could open up at Keystone.  Looks like they shut in last night early due to high nitrogen.  They do have a nom there today.  With my pressures I asked them to please open up, it would help me relieve my pressures.  He said that he would as long as the nitrogen doesn’t become a problem.

Moore



	0725
	Woodward 2
	Unit 4 is down.  Alan called and they are headed out.

Moore



	0835
	Oakland
	I asked Oakland to bring some units on the “BC” to “BC”.

Coash



	0951
	Bushton
	Terrell called in and said that the ESD was successful.  He said he’s opening the valves to common up the “E” and “D” south and the “E” north to make them common or bypass around the station.

Monden



	0958
	Ellis Co. 1
	Unit 1 is down.  Gary let me know that they’ve taken it down for a scheduled inspection.

Moore



	1000
	Warren Monument
	I received an alarm here, AC power fail.  Got a hold of the on call person Greg.  He said that either he or someone else would check it this morning.

Moore



	1020
	Bisti
	I’m doing a stop command on this unit remotely.  We’re taking it down due to this pig running that we’re doing on the San Juan lateral. We launched the pigs from Bloomfield at around 0830 this morning.  They had a pressure of 1180, flow of 865.  We’ll be running pigs up to Gallup.

Alvarado



	1121
	Bushton
	George Marshall came out and told me that all of the scada is now back up coming into Houston.

Monden



	1120
	El Paso Keystone
	Received a call from Randy.  He informed me that the nitrogen there is up to about 3.5.  He said that it was hurting them.  He is going to watch it for the next ½ hour and if he doesn’t see it come down then they would probably have to shut in the point.  I left a message and let Gary Spraggins know.

Moore



	1127
	Ellis Co. 3
	Unit 6 is down.  Steve called.  It’s for maintenance for 1-2 hours.

Moore



	1201
	El Paso Keystone
	That point is at zero flow now.  They shut in because of the nitrogen.

Moore



	1215
	Transok Sandstone
	They had a nom change of 10 million going to them.  I talked with Chuck over there and talked with Gary Spraggins also.  We’re just going to bank that until tomorrow.

Moore



	1300
	Beatrice
	They’ve completed the “B” line casing removal north of Beatrice.  They are shut in between valves 1 and 3.  They are going to open valves 1 and 3 at this time.

Coash



	1347
	Gallup
	The Gallup unit is being taken down at this time to allow the pigs to come in.

Alvarado



	1457
	Bushton
	Asked Terrell to split out the “A”, “B” and “C” at Bushton.  Also at this time I called Clifton and spoke to Deanna.  Asked her to shut the units down and split out the “B” and the “C”.

Monden



	1500
	Palmyra
	They’re going to split out their “E” and “D” suctions and common the “D” with the “BC” suction and shut one unit down on the “A” to “BC”.

Coash



	1515
	Beatrice
	They are going to crack some of the Trailblazer gas into the “B” discharge and shut down “BC” to “B” units and split out the “BC”, common the Trailblazer suction with the “D” suction.

Coash



	1556
	Clifton
	Deanna called in and said that she has all of the units down and the “B” and “C” lines are split out.  Everything is back like it was before they started doing the pipeline configuration for the outage for Bushton.

Monden



	1610
	Bushton
	Terrell has the “A”, “B”, and “C” lines all split out.

Monden



	1527
	Spearman
	Got an alarm in here that unit 3 has gone down.  I talked with the on call person Ronald.  He said that they had been working on that.  They tried to run it and it went back down.  It will stay down.

Moore



	1630
	Clark Co. 2
	Received a call from Dale.  He let me know that the moisture monitor is back in service.

Moore



	1708
	Ellis Co. 3
	Unit 6 is back on line.  Steve called in.  He had to change the water pump.  He’s going to the house.

Moore



	1754
	Mullinville
	On the lean stream Mike said that he has a high H2S of 4.57 ppm.  Told the south operator that the last time they had this that they traced it down to coming in at the TW Beaver interconnect and that would probably be a good starting point.  Looking at Beaver plant, coming up the “A” and the “B” I see no signs of H2S at those points.

Monden




1830 to 0630 Shift Thurs., Oct. 11, 2001  (Munson, Cummings, Welsh, Calhoun)

	1858
	Sublette
	Unit 23 is down.  The Sublette on call person checked in with me.  They are going to go take care of it.

Munson



	1915
	Mullinville
	Brian at Mullinville pulled two stain tubes on the lean stream discharge looking for H2S.  He came up with nothing on his stain tubes however his monitor still shows about 4.5.  I received word from Ed on the south end that Dennis Hall went to the TW Beaver interconnect and he pulled a stain tube there and it show between 2-3 ppm at that interconnect.

Munson



	1930
	Sublette
	Rick has unit 23 up.

Munson



	2010
	
	Seminole went down, not sure why.  Pat with the team is on his way out there and will try to get it started right back up.

Welsh



	2240
	Pony Express
	We had nom change on the late numbers at Pony Express.  The numbers went up about 3 million.  I called John at KN and asked him if he would bump that flow rate up over there to make rate for the day.  I also pointed out that we came in just about 3 million short yesterday and told him that if he wanted to flow above and beyond today’s rate by 2-3 million it would help make some of that up from yesterday.  He said that he would definitely try for the 58 to make today’s rate and if he had any gas available he would go for the small amount of makeup needed.

Munson



	2245
	
	I received a call from the Holcomb plant operator regarding some questions that she had about a possible security issue out of the Panhandle region.  I pursued this by calling Randy Lebeau, the director of the Amarillo region.  Randy informed me that he was aware of this security issue.  He termed it a non-emergency security issue.  He said that he was working with is fellow field operations personnel and local authorities to determine whether this was rumor or something that they needed to pursue.  Randy notified Dan Pribble and Mike Nelson.  Randy assured me that it would be taken care of out of his group.  He also let me know that Mike Nelson would contact Corporate Security.  This was my main concern, that any kind of rumors or issues be pursued by Corporate Security. Randy assured me that he passed it on to Mike Nelson and he is the Corporate Security contact for their group.

Munson



	2345
	Finney Co. 4
	Dave Powers checked in from Finney 4 to say that they had units 2, 3 and 4 on line and that unit 1 will remain down for the rest of the night.  He and his crew were leaving the site at this time.  I passed this information on to Arnie at Holcomb.

Munson



	1835
	Palmyra
	Had to call Mike Butts out to common up the “D” line with the “BC” suctions.  Also he was going to put another unit on the “BCD” common suction to “D” discharge.

Calhoun



	1930
	Great Lakes

TransCanada
	Their flow rate was 55, went to zero at Carlton.  I called them.  They said they lost HP and they’d have it back on.  The flow rate should come back up soon.

Calhoun



	2040
	LS Power Whitewater
	The operator called and said they were shutting in for the night and they will be back on about 6:30 in the morning.

Calhoun



	0000
	
	We have Seminole back on line.  In the process of losing Seminole we did lose some volume at Norval Pecos, Westar Reeves, Coronado Pecos, Valero Spraberry.  We did ask El Paso to take some gas at Keystone to sort of help us out for a little bit and they did.  We’ll balance that volume.  We did owe them gas there.  They just didn’t take it earlier because of the nitrogen but tonight they didn’t have a problem with taking some extra.  In addition to that we did have some problems with Valero Spraberry not due to the Seminole problem but the pressure on their side.  They had some problems.  We called them several times and they eventually pulled their pressure down and we did begin to flow probably around midnight.  As the pressure comes down we’ll continue to flow more but we do owe them quite a bit at the interconnect. We’re doing everything we can to give them that volume.  Needless to say we did experience high pressures at Plains and at Spraberry.  We did call Andrew out at Plainview point to take the regulator out of service so we could get some more volume through there for a short while and then he put it back in.  Seminole is restored and we are building up our pressure and we’ll make adjustments to see if we can get our deliveries back in order by 9:00 in the morning.

Welsh



	0235
	Waterloo
	Shut unit #7 down.  We were stacking up out at Earlville and Galena.

Calhoun



	0400
	Jal
	Unit #2 went down.  We called Kay with the Jal team.  She is on her way out to see if she can start it back up.  We called Sid Richardson and told them it was down.

Welsh



	0440
	Wisconsin Gas
	Gas controller called in concerning the Eagle interconnect.  They had a problem on their side where they couldn’t get all of their flow through.  They had a problem with the flow controller and they were running a little bit short this morning.  They were wanting us to bump our setpoint up from 72 to 77 million.  Coash had already talked to Gary Spraggins about it and said if we had the gas out there that we could surely help them out so that they could get their pressures back up and come in on rate.  So I went ahead and bumped it to 77.

Calhoun



	0530
	PEPL
	They had a problem with their meter at the interconnect.  Flow rate went to zero last night.  They ended up flowing about 10 million on an order of 17.  They are going to try to get that flow back on today and make it up.

Munson




slb  


