[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Tues., March 12, 2002  (Hardy, Henley, Spain, Monden, Muntz)

	0745
	Perryton Barlow
	Units 1 and 2 are down at Perryton Barlow.  The flow rate has gone to zero in preparation for the “A” line repair south of Beaver from block valve 10 into the Beaver yard.

Muntz



	0802
	Northrop
	Units 1 and 2 are shut down in preparation for today’s outage on the “A” line south of Beaver.

Muntz



	0810
	Needles
	Randy called in and said they will be calibrating transmitters at SoCal Needles interconnect the majority of the day.

Monden



	0828
	Station 3
	They’ve shut down unit #3 to do their minor maintenance on the unit. Estimated time is four hours.

Monden



	0830
	Cunningham
	I just called and gave Lynn an order to shut the injection rate in.  We were doing about 256.  We’re calling for 100 million withdrawal today in the plan but I’m just going to shut it in for now.  We’re supposed to get 140 less coming from Beaver.  We’ll see how it works out, see if we can get around 950 through Clifton.  Right now we’re doing about 890.

Spain



	0830
	
	I spoke to Darrel at Macksville.  I asked him to coordinate with Cunningham, when he sees the injection rate go to zero to go ahead and bypass the station.  We got scheduled about 360 coming from the south.  It’s not enough to support the Macksville turbines.

Spain



	0845
	Atoka 3
	Unit 762 down for minor maintenance.  They’re going to work on exhaust, change studs on compressor valve caps.  Spoke with Jerry.

Monden



	0914
	Crawford
	Unit #2 is on line at 0840.  Spoke with Bennie.

Monden



	0926
	NGPL Eddy
	Spoke with Darla. Their field had called her and said they are having problems with a coupling on a unit at Eddy and that they will need an estimated four hours.  During that four hours, nom is 25.8 MMBtu, they will move that gas and give it to us at Winkler for the four-hour period and then move it back up to Eddy and then cut back at Winkler.  I had no problem with this at this time.

Monden



	1033
	WFS Milagro
	Spoke with Mike in their gas control.  He said that they have a unit down at Ignacio and they will try to get the majority of our gas through Milagro.

Monden



	1043
	Beaver Continental
	Continental has a 1 million order on the “A” line.  Currently we are working on an outage south of Beaver plant on the “A” line.  I spoke with Gary and he said it would be OK to have them go ahead and shut in on the “A” line.  I called Ronnie Ashcroft back and let him know that they could go ahead and shut down on the “A” line.  Currently we show an order of 31 on the “B”.  We’ll go ahead and keep the “B” as the order.

Muntz



	1030
	Clifton
	I started unit #31 on the “E” line service.

Spain



	1308
	WFS
	It is running short by approximately 40 million on the nom.  I spoke with Mike Ellington in their gas control.  He told me that he has a lot of substations down and that they would get them back up as soon as possible.  They are doing some pigging.  Also they still have the unit down at Ignacio which I couldn’t get any extra gas up there at Ignacio.

Monden



	1308
	
	PNM called, spoke with Paul.  He asked if we could give him some extra gas for awhile until WFS got some of their HP back up.  He said he was hurting for some gas for his deliveries.  I told him we’d try to accommodate him until the HP with WFS comes back up but I stressed that we still had to come in on the nom and the 5 million under.

Monden



	1330
	Burdett
	Floyd just called in.  He informed me that they had a BSD.  I called Holcomb and informed them that they might see a little rollback.  Floyd said he should have the station back on line within 15-20 minutes so it shouldn’t cause any problems.

Spain



	1400
	P3
	Asked Denny on the P3 team to put on another small unit.  I just can’t make it by pushing the gas up from Roswell.  I have concerns of pressuring out Red Bluff and Bitter Lakes.  My discharge from Roswell is 984.  Had him put a unit on there to help distribute the pack more evenly on the Panhandle lateral, in turn lowering the pressure at Bitter Lakes and Red Bluff.

Monden



	1425
	Mullinville
	Dee called in from Mullinville. He asked me why his Texas “A” line was going down.  I informed him it was because of the Beaver drip outage that was going on down there, for him to go ahead and drop one of the Texas “A” to “D” units.

Spain



	1430
	P3
	Denny got a small unit on, #4 at 1415.

Monden 



	1521
	Pampa
	Jerry Dyson called in from Pampa and said that they 30”  KB was going to have to be exposed for several days.  Oneok crosses under the KB line and they have a leak on their line. He is going to get some further information on the block valves and will let us know the block valve numbers.  He said it would be between the airport block valve and Bobbit.  I conferenced in Jerry Graves on the call.  Jerry said he would get the information out to everybody also.  I am going to notify Beaver’s operator and let them know about it.

Muntz



	1541
	PG&E Topock
	Andy in their gas control had called.  He said they have a pipeline event, that they need some serious help in cutting back on the flow that we are giving to them because of compressor problems.  He requested that we come in short on the present day by about 25 million.  I see no problem at this time due to the fact that WFS is shorting us approximately 30 million at present.  I did also forward this information on to Jerry Graves so he would be aware of the issue.

Monden



	1611
	WFS
	Spoke with Francis in their gas control, that they were coming in short by roughly 20 million off the nom.  Presently needed to be flowing 30 million extra.  He said that the noms will probably be reduced.

Monden



	1620
	Jal
	I have an ESD bypass alarm at Jal.  I contacted OCC and had them contact someone from the Jal team.  Rick called in and said that the station actually did ESD.  The station was down, no demand.  He said they were going to leave it blown down this evening and would be out in the morning, would we load the pipe in the morning.  He said if we ended up needing to run the station later this evening to contact OCC and they would have some guys go out and load the station this evening.

Muntz



	1625
	Seminole
	I received a call from Bobby King Jr., Denver City, phone 915-758-9481. He said that he has an irrigation pipe that’s leaking in the southwest quarter of section 10, block A-8.  He said that they needed to dig out the line and he thought it ran underneath our pipe.  Contacted OCC and they had Vincent Diaz of Seminole give me a call. He’s going to check with Bobby King and get back with me as to what they decide to do with it this evening.

Muntz



	1620
	Forest Lake #1
	Dave with NSP called in and said the inlet pressure was dropping down there pretty fast.  It was holding steady at 60 and then dropped down to 49 and then 45.  I called Ted and Greg with the North Branch team.  Greg is going out to take a look at it and find out what the problem is.

Hardy



	1636
	Highlands Crawford
	Bennie Neatherlin with WT1, Carlsbad team had called in about this interconnect and was expressing some control issues.  When I spoke with him I asked him about the water because we were showing around 22# of water and they were flowing about 51 million at present.  He said he pulled a tube and on the tube they were showing about 18#.  I got a conference call with Bennie, Jerry, Darrell and Johnny Lamb with Duke Highlands.  We expressed our concerns of the high water to Johnny Lamb.  He said they would make their rounds to all of their dehys that feed into this interconnect and get back with Bennie on it.  Bennie will get back with gas control.

Monden



	1720
	Atoka 3
	Unit 762 is back on line at 1630.  Mondo called it in.

Monden



	1723
	GPM Zia
	On the measurement the gas temperature is running 142.  Spoke with Bennie on the Carlsbad team about this.  He said that he doesn’t see it as an immediate issue but he will address it in the morning when he goes to work.

Monden



	1741
	Highlands Crawford
	Johnny Lamb called Bennie back.  Told him that at his points that interconnect in the pipe that he had 10# at one dehy and 6# at Black River and he felt like the moisture would go ahead and drop down and get more compliant within tariff.  Bennie will check it first thing in the morning.  Then we will address the water issue again.

Monden




1830 to 0630 Shift Tues., March 12, 2002  ()

	1815
	
	PG&E called and said they needed us to cut a little bit more with the 25 million that was originally agreed upon to help them out with their situation.  I told them that I could probably do about 15 for right now and will look over my system and see whether or not that would affect me any on my pressures.  Right now we have a total of about 40 million short for PG&E Topock.  He said the problem may last for a couple of hours or so, the additional 15 million cut.  I will check back with him to see the developments on his system and see where we go from there.

Braswell



	1739
	NSP Viking Chisago
	They matched their nom for the day and shut in.  They ended up at 6 million.

Calhoun



	1815
	Palmyra
	Shut down unit #22.  That was on the “CD” to “D” discharge.  We had high differential, spread across the units.  Also we were building on the “D” line and “BC” so we really didn’t need it going north at this time.

Calhoun



	1840
	Harrisburg
	Called the on call person.  Told him that we were pinching out Aberdeen. Asked him if they could set the yard back up by shutting the valve and using the regulator to feed gas on out towards Brookings and let the Aberdeen gas to come in.  He was going to go out there and get the yard set up for that.

Calhoun



	1910
	Farmington
	We lost the inlet pressure and the delivery pressure out at SP1Q.  I got a hold of Tim Pietsch.  He went out to the station and pulled it up on the computer and he was seeing the same thing.  It looks like we haven’t had any updates since about 1650.  He was able to get a hold of NSP and talked to Gene the gas controller.  They also watched that point.  He said he had all of his data.  Tim said he would wait until morning before he goes out there to see if he can fix the RTU there.  He figures he had blown a fuse or something. But if we need any of that information all we have to do is talk with Gene at NSP.

Calhoun



	2110
	LS Power Whitewater
	Got a call from the operator.  He said they were on the way to shutting down for the evening.  They were going to start about 4:40 in the morning.

Calhoun



	2100
	Continental
	On the Continental “C” line we have a scheduled rate of 46 million for current day.  Currently receiving 21.  I spoke with the plant operator with Continental.  They said they are showing a 37 scheduled.  We are doing fine on the “A” and “B” lines as far as scheduled rate.  He said he didn’t have enough gas to actually give us the 46 on the “C” line however he said he would raise it up since they were only giving us 21 million.  It looks like we’re still going to be about 15 million short.  Notified scheduling and Gary Spraggins.

Barry



	2150
	Phillips Plymouth
	Have a schedule of 11 million.  We’ve been averaging 19 for the current day.  I tried to call their plant, got no answer, to request them to cut back to rate.

Barry



	2235
	Farmington
	I took unit #6 down.  It was on the “BC” discharge.  Load had died off and we were starting to pack up.  Didn’t need it.

Calhoun



	2245
	North Branch
	Shut down unit #4 that was pumping out west.  Temperatures were still warm up in the market area and had plenty of pressure at Benson and I was still packing up going out west so I took the unit off line.

Calhoun



	2328
	Farmington
	Shut down unit #3.  The west discharge going out to Willmar had packed up and we were still building on the “BC” going north.  Didn’t need the unit on.

Calhoun



	0005
	Monument
	Received a station alarm.  Called the OCC for the on call.  They got a hold of Bennie who called in.  I told him that I had received the alarm out there.  He said some people had been working on some things out there today and that they will check it out in the morning.

Braswell



	0023
	NSP Viking
	They brought their flow rate back up at the Chisago point.  They went from zero to 15.  What they are trying to do is get to their total nom there and they are going to batch it and shut it back in.

Calhoun



	0045
	Minnegasco
	They brought back 40 million to inject at Glenwood.  We were already doing 19 million there so I had to kick it up to 140 million to come in on rate for the day.

Calhoun



	0223
	NSP Viking
	They shut their flow rate in at Chisago.  They had batched a 7.2 rate.

Calhoun



	0415
	LS Power Whitewater
	They brought a unit on line.

Calhoun



	0445
	Ventura
	Got a call from Jerry with NBPL.  He said that CC was ready to start testing there.  We brought the flow rate up there by 30 million so that we could come in for the new rate on the day.

Calhoun



	0505
	Belleville
	Shut down unit #2 which was in series and put on unit #1 in parallel.  That way we’d have two units running in parallel and could flow the higher flow rate.

Calhoun



	0535
	Madison
	They called up and wanted to go from 58 million down to 43.

Calhoun




slb


