[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Tues., Feb. 26, 2002  (Moore, Alvarado, Barnes, Coash)

	0710
	Atoka 1
	We got the unit back on line there.  I received a call from Dagger Draw complaining about their pressure being high.  I looked at the trends and it’s looks like it is possibly because of the unit down at Atoka 1 it has backed into 3.  I doesn’t look like I have a unit down at 3 however I did make a call to Jerry to let them know that because I did receive two calls from Dagger plant.  He is going to go out and check to make sure.

Moore



	0558
	Stevens Co. 6
	Unit 4 down and the operator is in route.

Barnes



	0714
	Sublette
	Mike Burnam called to say that Sublette unit on the “A” line, #21, is down as well as unit 23 on the Haskell line due to Oneok shorting us gas.  They probably had freeze-ups in the field.

Barnes



	0722
	Texas Co. 2
	Oneok field supply gas that has been short through the night is now returning.

Barnes



	0722
	Beaver Co. 6
	Unit 2 has gone down. Dennis Hall will be going out.

Alvarado



	0806
	Beaver Co. 6
	Unit 2 is back on.

Alvarado



	0752
	Station 2
	Received a station alarm.  I talked with Hank there.  He is going to get that cleared.

Moore



	0825
	
	It looks like we lost unit 2 at Maljamar.  I gave a call to Conoco and talked with Ryan.  He said they had lost some units there due to some freeze-ups.  They’ve got people working on it.  He asked if we’d send someone to Maljamar.  He should have some gas by the time they get their.  I got a hold of Bob.  Either he or Randy will be going out to Maljamar station.

Moore



	0840
	Dagger 
	I received a call from them, second or third time, complaining about the pressure.  I’m showing their pressure has come down.  Right now I’m showing 624 which it looks like at 0530 this morning it was as high as 702.  I told him again that we had a unit down at Atoka 2.  The unit was back on earlier and it is pulling that pressure back down.  He said that he’s got a valve pinched back but he’s going to open up and that we will see a big difference which at this time they’re flowing 29.5 on 33.4 nom.  So we’re not far off from where we need to be.  I did tell him that I sent a person out to Atoka 3.  It has been checked and all units are on line, per Jerry.  We’ll see what happens.

Moore



	0844
	
	Pampa turbine down.  No demand for this unit at this time.

Alvarado



	0910
	Llano Lea
	I contacted Llano Lea gas control and spoke with Doug Atwood.  I advised him that they were under nom.  They have a 40 nom and right now they’re doing 27.3 on MMBtu rate and 25.8 on MMcf.  He said that they are having unit problems.  This might be continuing through the day.  He said they would try to make up later on this evening.

Alvarado



	0840
	Stevens Co. 6
	One unit there is down with electrical problems and another unit will not roll well to start, it’s too cold.  Advised Gary Spraggins and he will change the nom from 17 to 10.

Barnes



	0855
	Morton Co. 1
	Unit 4 down.  Men on location.  No answer when I called.

Barnes



	0902
	Hugoton
	Unit 2 on.

Barnes



	0902
	Stevens Co. 1
	Unit 2 down.  Men on location.

Barnes



	0911
	Finney Co. 4
	Unit 3 down.  I spoke with operator and he’s in route to the location now.

Barnes



	0914
	Hugoton
	Unit 3 down.

Barnes



	0917
	Stevens Co. 2
	Unit 8 down.

Barnes



	0931
	Finney Co. 2
	H2S is .455 grains.

Barnes



	0934
	Stevens Co. 2
	Unit 7 on.

Barnes



	0942
	Finney Co. 2
	H2S is now .06 grains.

Barnes



	0955
	Stevens Co. 6
	They units 3, 4 and 5 on for moving 9.5.  That’s all they can move at this pressure.  The pressure is 19# and it’s normally 24#.

Barnes



	0955
	Finney Co. 4
	Unit 3 on.

Barnes



	1000
	Lone Star Pecos
	I talked with Leslie there.  They changed the plate.  He said we ought to be good for up to 120 flow there if needed.  We have a nom today of 99.7.  That’s the reason for the plate change.

Moore



	1023
	Atoka 3
	Received a call from Jerry.  He let me know that he did go back out.  He found that there must have been a valve that had froze up on the high side suction.  It did cause the unit to go down after he had left.  He’s got everything fixed there and has the unit back up.  He said he would call the Dagger plant and let them know what the problem was.

Moore



	1025
	Amoco LaPlata
	I called and talked to Grant.  They are running behind.  I’m showing a flow needed of about 160 and they’re doing about 140.  The nom is 157.  He said that they have some problems, have some units down but they are working on it and we should see that come up soon.

Moore



	1025
	Meridian
	Called out and talked to Mary at Meridian.  Flow needed is about 160 and they are doing 148 on 160 nom.  She said they have compressors down and they are working on it.

Moore



	1026
	WFS
	Called out and talked to Ron. They are behind also.  I’m showing overall flow needed is 486 and we’re doing 450.  It looks like they are behind at Milagro about 30 million.  I asked him if he was going to give me the gas.  He said they’ve had some freeze up problems and units down. He’s got people working on it.  He said he would try to get me 15 more now and the rest as soon as he can.

Moore



	1043
	Mullinville
	I advised Mike that the DAS for RTU MULI is not communicating.  He will check it out for possible reasons there as well as EDS is checking for problems on this side.

Barnes



	1051
	Texas Co. 1
	Unit swap, unit 2 on and unit 1 down.

Barnes



	1049
	Canadian River
	Received an alarm in here of units 1 and 3 down.  Got a hold of Terry and he said they will check it.

Moore



	1131
	Canadian River
	Received a call from Mike Flynn.  He let me know that the units went down on low suction.  He went ahead and started back up but he’s not going to load them up.  He’s going to let the pressure build some there but he does want to leave them down because it’s so cold.  He’ll let me know when he gets back out and gets them loaded up.  He did also say that he would contact Duke.

Moore



	1140
	Agave Long Arollo 
	I received a battery voltage high there.  I’m showing 15.1.  I got a hold of Jerry and he said they would check it.

Moore



	1132
	Beaver Co. 1
	Unit 2, 3 and 5 have gone down.

Alvarado



	1143
	Beaver Co. 1
	Unit #5 is back on.

Alvarado



	
	Beaver Co. 1
	Units 2 and 3 are back on.

Alvarado



	1215
	NGPL Gray
	Sent a zero setpoint in there this morning to shut that in at 9:00.  It looks like it could still be flowing there though.  I’m showing 8.9 to 9 million Btu flow rate but it has been locked in history most of the morning.  Got a hold of Joe Martinez and he’s going to go check it.

Moore



	1221
	Llano Lea
	I’ve received a delmar malfunction alarm along with a high H2S alarm.  I did contact Ray Nosef on his cell phone and he was pulling up to the interconnect.  He said he would check it out for us.  He said they have been having some problems with this delmar today.

Alvarado



	1302
	Canadian River
	Units are back up there.

Moore



	1328
	Santa Fe Bilbrey
	Received a station pressure alarm there where it had dropped down to below 400#.  I’m showing 380 at this time.  I made a call out and talked to Ernesto on the Carlsbad team.  He is going to get with Bennie.  They are going to make the call out and see what is causing that.

Moore



	1400
	Oakland
	He’s going to drop two units on the “BC” to try to back into Palmyra so he could build that Hooper system back up.

Coash



	1430
	Garner
	I asked Garner to come on for 100 withdrawal.

Coash



	1436
	Crawford
	Got a call from Ernesto.  He took unit 2 back down so all we have on line is unit 1.  There is not enough gas coming from Duke.  They have been in contact with them and they just haven’t been able to give him enough gas.  They are going to give it a little time and see if they can get some pressure to it and maybe later put the unit back on line.

Moore



	1450
	Santa Fe Billbrey
	Received a call from Bennie.  He let me know that the reason we’re seeing the low pressure out there is due to the cold weather.  He said since they are not flowing at that point that each time that it gets cold like this that I freezes up easily because there is a lot of moisture there.  He said if it doesn’t clear up through tonight that they will look at it tomorrow.

Moore



	1515
	Station 4
	Just received a call.  They let me know that they had to take unit 2 down for a little while.  Unit 1 has an unloader problem and unit 2 has a bad switch.  They are going to have both units down for a little while so we’ll only have unit 3 on line there.  So he’s going to do some maintenance there and then they will bring one of the units back on line.

Moore



	1525
	Martin Co. 1
	I spoke with Tom Hatfield about our pressure getting out of calibration.  He thinks that it might be a pressure transmitter problem.  He said it may be happening also due to the cold weather that we’ve got in the area.  We’re going to go ahead and let it ride for tonight.  He said if it gets real bad he will check into it in the morning.

Alvarado



	1529
	Ellis Co. 2
	Unit 4 is going to be taken down. Wayne called in and said that they don’t have enough gas to run the unit.  They have some gas that is freezing off back behind the unit out in the field.  He said they will put this unit back on when they get the gas back.

Alvarado



	1541
	Woodward Co. 1
	Unit 3 has gone down. Alan was paged through their 911 system.  He’s got some field personnel heading over there.

Alvarado



	1600
	Ellis Co. 1
	Unit #3 is going to stay down due to some frozen tubing lines on the unit.  They are going to try and thaw these out tomorrow morning, per Wayne Pitts with the Ellis Co. 1 team.

Alvarado



	1615
	Crawford
	Received a call from Darrell.  He let me know that he has unit 2 back on line there, that they believe they have enough gas to keep both units on now.  Both 1 and 2 are on line.

Moore



	1620
	Conoco Maljamar
	Received a call from Ryan.  He let me know that they’ve got their problem fixed at the plant.  They are getting ready to send us some gas.  I did let him know that we do still have a unit on at Maljamar that is idling.

Moore



	1640
	Station 8
	Received a unit alarm on #1.  Made a call out and talked with Ron.  He said that they did some work on the unit and they are pressuring it back up.  They will let me know when they are finished.

Moore



	1649
	Canadian River
	We do have both units 1 and 3 back on line there.

Moore



	1647
	Red Cedar
	The CO2 came up to 2.92.  I made a call out and talked with Delbert.  I asked him to get that down to 2.8 or less preferably.

Moore




1830 to 0630 Shift Tues., Feb. 26, 2002  (Calhoun, Cummings, Davis, Munson, Welsh)

	1845
	Stevens Co. 1
	I talked to Anthony Sandoval.  They had lost unit #6 at Stevens 1.  It had bearing sensors that had failed.  They were trying to get unit #4 up and on line.  They were letting the oil warm up.  At 1902 they did put unit #4 on line.

Calhoun



	1845
	Stevens Co. 4
	Unit #4 was down.  I talked to Mike Zielke.  He was over at Stevens Co. 1.  He said on his way home he was going to stop by at Stevens Co. 4 to see if he could load up what units he had on because the suction pressure had been coming up at the station.  If he had to he was going to put unit #4 back on also.

Calhoun



	1856
	Stevens Co. 4
	Got a dehy failure.  I notified Mike Zielke.

Calhoun



	1845
	Sublette
	Oneok was having problems getting their units on at Haskell Co.  Their instrument air had froze off.  Unit #24 at the station at Sublette went down.

Calhoun



	1945
	Sublette
	Talked to Frank Velasquez.  Oneok had their units back on and he was on his way out to the station.  I went ahead and put a remote start in on unit #24.  He was going to check the unit when he got there and make sure it started.  Also he thought he might have to put unit #23 on line with it.

Calhoun



	2005
	Holcomb
	Talked to Arnie.   Tate suction pressure was coming up so her to load the units up and speed them up because we were needing the gas up at Bushton.

Calhoun



	2011
	Stevens Co. 4
	Talked to Mike Zielke.  He got unit #4 back on line.  Oneok finally got a unit back on and got some suction.

Calhoun



	2026
	Stevens Co. 4
	They got the dehy back on line.

Calhoun



	2041
	
	Asked LNG to shut in.  I think we’ve got this under control.

Cummings



	1930
	Maljamar
	The Conoco plant flow rate has gone to zero.  The plant has gone sour and Randy is on his way over there at this time.  He’s been in touch with Ryan at the plant.

Munson



	1930
	
	We have unit #2 down at WT2.  Shane is going to take care of that.

Munson



	2050
	Maljamar
	Randy is still on site at Maljamar.  He had flow recovered at the plant but they went sour again and the flow went to zero.  Our unit is remaining on because it goes into recycle every time the flow goes away.  Randy is going to remain on site for a little while longer and hopefully the plant will get lined out.  Randy has been in touch with Ryan at the Conoco plant trying to work things out.

Munson



	2050
	WT2
	Shane has the #2 unit back on line.  He’s headed over to the Kermit turbine on the Permian end.  I passed that information on to Ed.

Munson



	2100
	Sublette
	Frank had lost unit #23.  He went out and got it put back on.

Calhoun



	2135
	Tescott
	Talked to Gary.  He was going out and put unit #3 on the “D” line.

Calhoun



	0232
	Beaver Co. 5
	Unit 4 went down.  Dennis Hall called in.  They are going to leave it down.  It went down due to low suction.  He will start that up first thing this morning.

Welsh



	0230
	P3
	Tony went out and took down unit #2 at P3, no demand.

Munson



	0255
	PG&E Topock
	Art with PG&E called and asked for help.  He said that his system has become very packed up overnight and he asked if we could short him some gas and under deliver in order to help him loosen his system up.  I offered to cut 15 off the spot and go from 182 to 167 flow rate.  He said that would be fine.  I told him if I could do more later I would give him a call back but this will come out to a number of 5 million off the nom for a 24-hour period.

Munson



	0320
	Valero Ward
	The flow rate at Valero Ward just went to zero.  I notified Ray at Valero gas control.  He said that he would send someone out.  It’s most likely going to be that malfunction that they have on their H2S.

Munson



	2055
	Morton Co. 6
	Unit #2 went down.  Ron Olson was on the way out there.

Calhoun



	2319
	Sublette
	Lost unit #23 again.  Frank got it on at 2340.

Calhoun



	2344
	Tescott
	They finally got unit #3 on the “D” line.

Calhoun



	0254
	Morton Co. 6
	They got unit #2 back on line.  They said the unit was froze up.  They had to get it all thawed out before they could get it on.

Calhoun



	0440
	Valero Ward
	Valero has the valve back open at Ward.  We’re flowing gas.

Munson



	0403
	Stevens Co. 2
	Lost unit #6.  They were going out to put it on.

Calhoun



	0540
	WT2
	Unit #2 has gone down.  I notified Joey Green.

Munson



	0602
	P3
	Unit #5 has just gone down.  I notified Tony.  He’s going to go take care of it.

Munson



	0559
	Sublette
	Lost unit #21 on the “A” line field service.  Frank was going out there to get it put back on.

Calhoun




slb  

