[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Sat., Jan. 19, 2002  (Cochran, Barnes, Coash, Alvarado, Moore)

	0550
	Station 5
	Received a station alarm and a BSD alarm.  Got a hold of the on call.  Eugene is headed out.

Moore



	0553
	Bloomfield
	I received a unit 4 alarm and a station alarm there.  I got a hold of Blackie the on call.  He’s headed out.

Moore



	0630
	Gallup
	I received a unit alarm there.  I talked with Pat.  He’s going to go out and check it.  He said it’s probably due to low surge margin, down to about 18.

More



	0637
	Station 5
	Received a call back from Eugene.  He let me know that the alarm there is on a valve position alarm on valve #5006 which is the mainline.  He said there is no problems there.  This is due to a wiring problem.  They do have an outage scheduled for Tuesday and he’s going to make note to get that fixed.  We will see the alarm until that time.  He did say if we needed the unit before they get this repaired that they would have to go out and do it before so.

Moore



	0810
	Redfield
	I just gave them an order to go from 375 down to 325.  Also visited with Jerry at Ogden.  Going to drop one of the horizontals going from Redfield to the “D” north.

Cochran



	0810
	Sublette
	ESD pressure is 139, down from 148# at 0300.  Advised the on call operator and he will check for possible freezes at the station and the ESD system.

Barnes



	0806
	WT2
	Unit 201 down.  Got a hold of John.  He’s headed out.  We did talk about it with the deliveries south of WT2 dropping off from 210 to 180.  We’re just going to leave that unit down and make the deliveries with unit 3. We’ll torque it out.

Moore



	1010
	WFS
	Received a call from Mike.  He asked me to put a zero setpoint in at LaMaquina.  They are still having problems there.  It had been flowing about 4-5 million but it looks like it may be unprocessed so we had to shut that in there.  We’re trying to do a little more at Milagro. To get closer on rate.  It may be several hours before they get LaMaquina back on.

Moore



	1003
	Red Cedar
	The CO2 came up there, showing about 3.1.  I made a call and talked with Jack and let him know.  He said he would get that down.

Moore



	1028
	Station 2
	Received a station alarm there earlier.  Wayne went out and got that cleared.  He decided he needed to go ahead and take unit 1 down to change filters because of the high differential.  He said it would be down for about ½ hour.

Moore



	1122
	Clifton
	Unit 29 down, no demand, by remote stop.

Barnes



	1130
	Cunningham
	Order changed from 500 withdrawal to 300 withdrawal.  Spot flow is 455.

Barnes



	1140
	Ogden
	Just had Jerry shut down the other horizontal going “BC” to “D” north, no demand.

Cochran



	1145
	Ventura
	Dropped unit #11, no demand.

Cochran



	1200
	Ventura
	Dropped unit #12, no demand.

Cochran



	1210
	Ventura
	Dropped units #13 and #15, no demand.  We’ll now bypass the station.

Cochran



	1230
	Minnegasco
	I just received a call from Danny.  They are cutting the Grundy receipt which is 28.9 million.  I visited with Jodi at NBPL and we went ahead and made the 30 million cut at Ventura to come in on rate for the day.

Cochran



	1320
	Station 5
	Had Eugene open up the mainline block valve there.  The station was bypassed.  In opening that block valve 5006 it cleared the alarms that we had gotten earlier.

Moore



	1340
	Station 7
	Had OCC get the on call person Norm.  Told him that I want to put a unit on at 7 to pull away pressure from 9.  I’m up to 1006 on the discharge and the _______ line checks at about 1008.

Moore



	1415
	Oakland
	Just visited with personnel there.  Requested they go ahead and shut the nine units down on the “BC” and go ahead and bypass.

Cochran



	1448
	Bushton
	Turbine unit #32 is down, no demand.  I requested it down at 1220.

Barnes



	1500
	Ogden
	I just shut unit #13 down going “BC” to “D” north.

Cochran



	1500
	Seminole
	Seminole unit is back on.  They took Seminole down at 0941 this morning to download a new program to the unit.  I did lose a small amount of delivery to Norval but I’m going to be able to make it up.

Alvarado



	1508
	Beaver Co. 5
	Unit #4 is back on.  This unit went down last night.  They elected to leave it down due to not enough gas out in the field so they let the field build back up.  Now they are bringing it back on.

Alvarado



	1510
	Faribault
	Just shut the unit down, no demand.

Cochran



	1510
	LaCrescent
	Just shut the unit down no demand.

Cochran



	1515
	Alexandria
	Shut the unit down, no demand.

Cochran



	1520
	Harrisburg
	Visited with Rick who takes care of that.  He is going to go back out there and put the Harrisburg regulator back in service.  Aberdeen is starting to pressure out some due to the warmer weather.  He is going to put the regulator back in service and take care of it.

Cochran



	1535
	Ogden
	Just shut unit #16 down going “BC” to the east, no demand.

Cochran



	1540
	Seminole
	Jerry is requesting me to go ahead and take Seminole back down.  They’ve got to do one more minor program load to the unit and then they’ll be bringing it back on.

Alvarado



	1620
	Guthrie
	Just shut the unit down, no demand.

Cochran



	1640
	Station 7
	Still don’t have that unit on line there.  I made a call out and talked with Kevin.  He said he tried to start one time but didn’t make it.  He’s waiting on the air right now.  He said he should be able to try again in 2-3 minutes.  I let him know that my pressure at station 9 is 1008 discharge and I’m at 1010 on the mainline behind check at 9.  Need it ASAP.

Moore



	1655
	PNM Rio Puerco
	I made over there and talked with Brent.  Asked him if I could raise up at Rio Puerco and cut some at the hub to try and help relieve my pressures.  We still haven’t got a unit on at 7.

Moore



	1711
	Seminole
	The Seminole unit is back on.

Alvarado



	1711
	GPM Linam Ranch
	I’ve contacted Ray Nosef to go out to Linam Ranch interconnect and shut down one of the meter runs.  We do not have enough gas to run both runs at this time and it’s alarming on low differential pressure going across the two runs.  Ray is going to go out and shut one of the runs in.  I advised him that it looks like we have the same amount of nomination of 29.7 for tomorrow as well.  The reason I didn’t send him out earlier is because GPM was over delivering to us and we were finally able to get them to come down to their nom for the day.  We’ll be able to close that one run now.

Alvarado




1830 to 0630 Shift Sat., Jan. 19, 2002  (Calhoun, Munson, Welsh, Cummings)

	1900
	Stevens Co. 6
	I received a high H2S alarm at Stevens 6.  I notified Craig through the OCC.  In the time that it took the OCC to find him the alarm cleared up.  I advised Craig of this.  He is not going to go out there.  He asked that we just continue to monitor it as usual and let him know if it spikes again.  He said he would pass it on to the team next week.  I did give him the numbers where it spiked up, from .15 and .2 range up to 1.8 and then back down to .18 and .15 range.

Munson



	1815
	Madison
	They called in and wanted to take their rate from 60 to 50.

Calhoun



	1854
	Farmington
	Took unit #3 down going to Willmar.  That’s because all three units were down on bottom and unloaded.  I got an alarm on the unit so I took it down and let the other units speed back up.

Calhoun



	1912
	Farmington
	Unit #5 – Took it down.  We were getting up on top on the “BC” going north.  I had plenty of pack up north at North Branch and also we were growing at Carlton.

Calhoun



	2000
	Beatrice
	Took down unit #27, the turbine on the high side.  They had backed off the “BC” at Oakland and also had dropped Guthrie Center to get off of Ogden.  It had rolled back at Palmyra so I dropped the turbine at Beatrice to help that situation.

Calhoun



	2005
	
	Station 8 lost it’s power.  It did ESD the fuel run system so I called Ron Arnold to visit on the phone and Troy Tucker to come out and help him.

Cummings



	1908
	
	Merlyn shut station 1 down for me.  The block valves did not open.  He worked quite awhile to get the station to where bypassed.

Cummings



	2100
	Seminole
	Jerry on the Seminole team said they needed to take Seminole down for approx. one hour while they fix a control on it.  Then they would be starting it back up.  We’ve alerted everybody that needs to know.  They said they would be done in about an hour.

Welsh



	2200
	LS Power Whitewater
	They called in and said they were shutting down for the night.  They were going to start back up about 1330 tomorrow afternoon.

Calhoun



	2400
	Skellytown
	H2O is 9.9#.  Dorchester delivers into that and it’s at 10# plus.  We called Eric Haiduk who seems to be the person out there that knows who to call.  He said he would call Cargray plant and see if they can find the problem and get it shut off.

Welsh



	0135
	Beaver Co. 5
	Unit 4 went down. We were instructed earlier today by Randy with that team to leave that unit down and they will start it up first thing in the morning.  I believe it goes down on low suction.  They prefer not to start it until daylight.

Welsh



	0230
	Skellytown
	Eric Haiduk with the Pampa team checked on the H2O monitor.  We were reading 10# here on our monitor.  He went out and actually pulled a tube on it and it was 2#.  He said he would go out in daylight tomorrow and dry it out and reset it to get a good reading.  He was quite a ways from there and it took him a long time to get out there and actually get to it but he said it’s really only reading 2# out there so we don’t have all of the moisture that we think we’re getting.

Welsh



	0210
	Seminole
	Jerry and Jim out on the Seminole team brought that unit back on.  It had been down since 2100 last night for work on their controls.  They said the only way it could be fixed was to take the unit down.  It took longer than they anticipated but the unit is back up.  We did lose some deliveries to Norval, seems to be the only one that suffered.  We reset the setpoint and they are coming up to rate right now to rate out by 9:00 in the morning.

Welsh



	0256
	Seminole
	Jim Myers called.  It looked like the unit went back down. They are still checking the problem.  They are not sure exactly what the problem is but there are people there and they are still working on that unit.  He said it would be approx. one hour.  Seminole is back down at 0256.

Welsh




slb  

