[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Fri., March 8, 2002  (Hall, Armitage, Braswell, Barry)

	0605
	
	I called WFS and NWPL gas controls and informed them that we are having to back some of the gas out of the LaPlata since we do have the electric unit down at Bloomfield.

Barry



	0615
	
	Called station 1 and requested unit 102 due to increase in deliveries this morning.

Barry



	0925
	Pierz
	Called the OCC.  They got a hold of Mark Werner for Pierz location.

Hall



	1040
	Warren Eunice
	Got a call from Debra Tower at Dynegy.  She informed us that a truck had hit one of the power poles out there at their interconnect with El Paso and knocked the power off out there.  They were delivering gas at the El Paso interconnect.  She was wondering if we could take some gas at the Warren Eunice plant until they get the power restored over there.  I conferenced her in with Richard on the TW board and decided that it was OK for them to do that as long as the gas wasn’t sour.  She said it wasn’t sour.  She doesn’t have a time frame right now as to when they may get the power restored but right now they are flowing about 15 million to us at the Warren Eunice plant.  I did notify Gary Spraggins, left a message on his voice mail, and notified scheduler Joe Linhart who said it was OK as well.

Braswell



	1435
	Ortenville SD

Harrisburg District
	There is no heater on this TBS.  The Vienna SD one does have a heater.  The on call was going to turn it over to the person who takes care of it and let him know.  The temperature on it was down to 10.49.

Hall



	1435
	Morgan TBS #1
	That belongs to the Welcome district.  There is no heater on it.  Fremont NE #1A in the South Sioux district.  Mike is the person on call.  They have a heater but it’s not on because the thermal coupler is not working and the manufacturer of heater is no longer in business.

Hall



	1435
	Evansville IA TBS
	Waterloo district – Rick said he would call Gary and have him check it out for us.  The temperature is running 19.7.

Hall



	1435
	EFM Lake Elmo #1B
	North Branch – Diane was the on call.  She called the person that takes care of it and will have them take care of the temperature problem on it.  It’s running 34.8 right now.

Hall



	1435
	Marystown MN
	Farmington District – They said not to worry about that one until it gets down to 10 degrees.

Hall



	1435
	Rochester South
	Owatonna District – Talked to Jim.  The temperature is running 10.4.  He said not to worry about it.

Hall



	1600
	Stevens 4
	Units 1, 2 and 4 are down due to a power failure.  As soon as they get the power failure problems solved Maurice will put the station back on line.

Armitage



	1744
	Garner
	Just got a call from Mike Woolery.  They’ve lost AC power and the plant is down.  The 100 million we were doing has gone away.  He’s calling the power company and he will get back with us as soon as we know something.

Hall



	1745
	Mapco NE TBS
	It belongs to the Beatrice plant.  Called the OCC and they go a hold of Don.  I told him that the problem out there is the battery voltage showing 10.9.  The low/low alarm is set at 11.  He is going to have somebody check it out for us.

Hall



	1748
	North Branch
	Called OCC and they got a hold of North Branch on call.  Center City and Isanti (?) #1 MN both showing low flow temperatures.  Center City and Isanti showing 19.0.

Hall



	1755
	North Branch
	Got a call from Jim.  He said the Center City and Isanti TBS’s should be OK with their temperatures.

Hall



	1757
	
	Got a call back from Mike Woolery at Garner.  He has his power back.  He doesn’t know for sure exactly what caused it to go. Lyons hasn’t been able to tell him.  He said that until he they do some troubleshooting and everything he was kind of reluctant to come back on right now.

Hall




1830 to 0630 Shift Fri., March 8, 2002  (Coash, Cochran, Spain, Barnes)

	1800
	Sublette
	Just lost unit #19.  Also at Stevens 2 we have units 6 and 11 down.  I called Maurice over at Stevens 4 to see if anybody was over there.  He said they are all up at 6 and they’re at 4 so he’s going to get a hold of somebody to go over to Stevens 2.  Also have one unit down at Stevens 6 and also a unit down at Steven 4 but people are working on those at this time.

Cochran



	1832
	Beaver Co. 13
	Unit #1 went down.  Mitchell is going out for us.

Spain



	1900
	Waterloo
	Bypassed the Waterloo station.  We were up on discharge at Galena, 870# suction.  Earlville is back on.

Coash



	1900
	Western Gas Midkif
	John Bigley called from the Midkif plant.  Their pressure came up real high.  It’s almost 800#.  For all appearances it looked like our positive shut-off valve closed on them, shut the flow off.  John is going to send some gas to El Paso to keep his reliefs from blowing off.  I called the Big Lake on call team and spoke to Larry Stroud.  He is going to go down there and look at the valve for us but right now we’ve probably got them shut off physically.

Spain



	1900
	Garner
	Garner had tripped off due to power problems.  They said the power company said the power should be available but may be undependable.  They can come back on if needed but we’re going to leave them shut in for right now.

Coash



	1920
	Maxus Dumas
	I got an H2S alarm there reading .64.  I called Don over at the Sunray plant.  He placed a call to the Maxus plant that was delivering the gas to us.  They informed him that they had a flame go out on an extractor or some of their equipment.  The wind has been blowing real hard up in that area all day, gusting up to 50 mph.  They informed Don that they do have the problem resolved and it should come back down.  It looked like it just spiked up there for a period of time.

Spain



	1945
	Beaver Co. 13
	Mitchell called back in.  The unit went down on low suction.  He’s not going to put it on, just leave it down.

Spain



	2005
	Perryton
	Unit #2 went down.  I also got an AC power failure.  Got an AC power failure both at Northrop and Perryton.  I called OCC.  Steve Rima called me back.  He informed me that they have to shut those stations down.  They can’t dehy any gas without power so he’ll put them back on when the power comes back on.

Spain



	2020
	Sunray
	Don called back in concerning the Maxus gas with the high H2S.  He ran a tube on it.  They were showing .14, down below tariff.  He also checked his commingle discharge and it was low, didn’t show any H2S in it.  It just apparently had a spike at the plant.  Looks like it’s back under control now.

Spain



	2030
	Plainview
	I noticed my flow went to zero at Plainview.  It was flowing about 180 million north.  I called OCC and got the on call person, spoke to Andrew.  He’s going to go out and check the measurement for us.  The pressures didn’t change upstream or downstream so it’s not a recycle valve failure or anything like that, just the measurement.

Spain



	2050
	Mennonite TBS
	I just called the OCC who called the on call tech. The temperature got down to 19 degrees.  We’ve had about a 40 degree ambient temperature drop out in that region the last two hours.  I wanted to make sure we didn’t have a heater or something that was out.  He said there is not a heater out there and the gas usually runs at whatever the ambient temperature is.  He said we should be OK.  I just wanted to double check and make sure we didn’t have something out and a freeze-off getting started.

Cochran



	2220
	Westar Carson
	I was showing a flow rate at Carson.  They don’t have any nom.  Shouldn’t be anything flow.  Also I got an alarm in here of 210# of water.  I called Westar.  They were looking at it through their system.  They were telling me that there wasn’t any flow at that point.  It must be bogus readings coming from our equipment.  I’ll pass that on to the day shift and have them check it out.

Spain



	2220
	Finney 3
	Had ESD and power failure and lost all of the units out there.  Personnel headed out there to see about getting it back up.

Cochran



	2220
	Stevens Co. 2
	Lost unit #11.  They may go ahead and leave that down due to lack of gas.  They are going to page the person that was out there earlier and let him know about it but that’s probably what they are going to end up doing.

Cochran



	2118
	Follett TBS
	Outlet temperature has dropped to 68 degrees.  85 degrees is the lowest it has been for the last three days and has been averaging 100 degrees.  Advised Mitchell Peil the on call.  He will check the heater.

Barnes



	2227
	El Paso Blanco
	My setpoint is not controlling the flow.  I advised Randy with El Paso gas control.  They own the equipment and he will have someone check it.

Barnes



	2229
	Follett TBS
	A heater fire was out.  Now it is re-lit and temperature is increasing.

Barnes



	2245
	Hugoton
	Lost unit #12.  Rocky Mason is headed out there to see about getting it back on.

Cochran



	2251
	PEPL Hansford
	POI 8042 – The flow is erratic and has been for some time now, several days.  Advised PEPL and he cannot poll it often enough to see this problem however he did agree to a higher flow rate to possibly stabilize the flow.  Today’s nom is 13.7.  Tomorrow’s nom is 81.7.

Barnes



	2315
	Altura
	That Oxy Permian plant up there has been trying to come on line for about an hour.  They called me and told me that they think our analyzer is keeping them shut in.  I called the on call person, spoke to Ray Nosef.  He said he would take a look at it for them.

Spain



	2330
	Wrenshall
	Asked them to shut in.  They are doing 100 withdrawal.

Coash



	2315
	Perryton Barlow
	Steve called in.  He’s got the units back on.  The AC came back on at both stations, Perryton and Northrop.  So he’s got all of the units on and the station is back to normal.

Spain



	2345
	Beaver Co. 7
	Unit #2 went down.  Mitchell is going to go out for us.

Spain



	2330
	
	PNM called to say they have asked USGT for 25 to them at Rio Puerco.  This would be a ride on the pipeline without gas coming in for that delivery.  Advised Darrell Schoolcraft and he OK’d it.

Barnes



	2340
	
	Tracy with Aquila called with her request for the 25 for PNM at Rio Puerco.  The agreement was made.

Barnes



	2340
	PNM Rio Puerco
	Began the delivery as agreed.

Barnes



	0004
	Gallup 
	Unit alarm – Advised Korey Kruse.

Barnes



	0050
	Plainview
	Andrew called in.  I had called him out earlier about 8:30 tonight concerning the measurement, north and south flow.  He informed me that the ultrasonic measurement they can’t fix it.  They’ll probably have to have a factory rep come out Monday.  So it looks like we’ll be running the weekend with no measurement going through Plainview.  We’ll just have to adjust the pressures, operate that way during the weekend.

Spain



	0058
	NGPL Eddy
	Flow is zero.  Their pressure has dropped of.

Barnes



	0108
	Gallup
	Unit alarm cleared by Korey Kruse.

Barnes



	0121
	El Paso Blanco
	Delivery is now back in flow control.  They had a technician do some repair on their equipment on location.

Barnes



	0328
	NGPL Eddy
	Flow rate returned with their increased line pressure, now back as anticipated.

Barnes




slb  

