[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Thurs., Feb. 21, 2002  ()

	0730
	Macksville
	OCC got a hold of the on call for us. I spoke with Bill. He’s going to put two units on the high side to help pull the pressure down for Cunningham and make it easier for the flow to come out.  I notified Doug at Cunningham and he’s looking for that.

Henley



	0845
	Ogden
	Got a hold the OCC. They got a hold of the on call, John.  He’s going to get a hold of a tech to take care of Ft. Dodge IA South battery voltage.  It’s showing low/low, showing a zero.  He said he would call me back and let me know who it is.

Hall



	0845
	Cloquette/Carlton
	Got a hold of the on call.  He transferred me over to Loren.  I passed on to him that the battery voltage is showing low/low, showing 10.9.

Hall



	0850
	Tescott
	Unit #5 went down.  I called the station and Gary is going to have Kim call me back.

Henley



	0853
	Tescott
	Unit #5 – Just spoke with Kim.  He said the reason the unit tripped was due to him taking an oil sample.  He did get it back on line so it is coming back up to speed.

Henley



	0917
	Ft. Dodge South
	Stacy just called from Ogden.  He’s going to go up and look to see if he can fix the battery charger on it.

Hall



	0940
	Burdett
	Lost unit #2.  Jay put unit 3 on in its place.  We’ll have units 3 and 4 running.  They are going to a safety meeting so we’ll be on our own.  If we need something we’ll have to contact OCC.

Henley



	1014
	Palmyra
	Received a t-control alarm.  I contacted the on call, spoke with Keith.  He said that he will pass that information on to Bob who is actually operating today.  He thinks that it is probably a generator alarm. He will get back with us.

Henley



	1140
	
	Talked to Amoco LaPlata.  I wanted to find out whether or not he was going to come up on nom today.  His nom is 157.  He told me that they were waiting on some more gas from Red Cedar.  They were shorting them.  I told him that they need to get up on nom.  He said he would try everything he could to get as close to rate as he can.  I did inform him that I will be calling Red Cedar to find out what was going on.

Braswell



	1145
	
	I talked to Red Cedar.  He was telling me that they have a unit that was down, scheduled for maintenance.  Also they had a tie-in that was going on out there today.  Of course this is causing their field pressure to be down, the reason why they weren’t able to come up on nom for right now.  He doesn’t expect it to last too much long, maybe another 1 to 1.5 hours.  Then he will try to get up as close as he can on rate.

Braswell



	1:15
	TransColorado
	Talked to Sam at Kinder-Morgan gas control.  He informed me that they were doing all that they can at the TransColorado point.  The nom is 91.2 million.  They are actually spotting right now about 71.9.  He said he had all of his HP on.  He did bring some gas from up north.  It’s just going to take awhile before we actually start seeing the flow come up, at least 24 hours but they are doing all that they can to get on that nom.  They are trying to talk to El Paso to see if they can cut them back a little bit so they can come in a little closer on their nom for us.

Braswell



	1325
	Black River Falls WI
	Got a low alarm on the station flow temperature.  Called the OCC.  They got a hold of the on call at Farmington.  He said that he would pass it on to the person who takes care of it who according to our records is Tim Pietsch.

Hall



	1426
	Station 4
	I’m showing all three units down at this time.  I called Howard.  He said they had some type of malfunction on the loop line.

Barry



	2:32
	Macksville
	Just spoke with Bill.  #3 unit had an oil leak.  He has tried to repair the oil leak and had to take the unit down and #2 went down on it’s own accord.  He will repair the oil leak and put the unit back on line.

Henley



	1710
	Pierz
	Called the OCC.  They got a hold of Jim.  I also called NSP and let them know that a unit had gone down at Pierz.  They were experiencing low pressure anyhow in that area.  They’ve had low pressure all over on their system today due to the loads.  I told Jim it looked like ours might have gone down because of the spread on the unit, it was spread out pretty good.  Had a little over a 200# spread between their pressure and our discharge.  North Branch had gone down earlier.  I told him I wasn’t in a read great hurry to go ahead and get the unit back on but we do need to try to get this gas in from NSP at Pierz.  He’s going to call Mark and see if he can get it reset from home or whatever needs to be done.

Hall




 1830 to 0630 Shift Thurs., Feb. 21, 2002  (Barnes, Alvarado, Moore, Cochran, Coash)

	1855
	Sublette
	Lost unit #21.  Rick Titus is going to go out there and see about getting it back on.

Cochran



	1815
	Spearman
	Unit 1 down.  Ronald the operator is in route.

Barnes



	1843
	Spearman 
	Unit 1 back on.

Barnes



	1915
	Plainview
	Station alarm cleared by Andrew.

Barnes



	2028
	Station 4
	Unit 402 has gone down.  I’ve contacted OCC.  I’m waiting to hear from the on call at this time.

Alvarado



	2125
	Maxus Dumas
	H2S jumped to .642 grains at a 18.5 flow rate. The 18.5 is also the average rate so far for the day.  I called their plant and they had a unit go down and they put it back on.  That’s the reason for the spike of H2S which they say is already coming down.  I also at that time notified the Sunray operator.

Barnes



	2147
	Maxus Dumas
	H2S at a .318 grains.

Barnes



	2147
	Plainview
	Station alarm – Advised Andrew.  He said it’s still related to some of the gas sniffer false readings that they’ve been getting out there.  It will stay in alarm through the night.

Barnes



	2157
	Sunray
	H2S of .40 grains.

Barnes



	2159
	Maxus 
	.046 grains.

Barnes



	2209
	Sunray
	H2S 0.128.

Barnes



	2206
	Skellytown
	Oxygen of 0.216%.  Our maximum allowable before calling someone is 0.210.  Advised Vance Griffith on the Pampa team.

Barnes



	2236
	Skellytown
	Oxygen is now 0.185% and well in range.

Barnes



	0117
	Phillips Plymouth
	POI 661012 – They received a pig at 0016 that overloaded the separators and dumps.  Thus, they slowed units, _____ liquids and stayed slowed until liquids are again manageable.  The flow rate at this time has dropped from 25 to 12.  They will resume as soon as possible.

Barnes



	0150
	Hugoton
	Lost unit #14 out there.  Personnel is headed out to see about getting it back on.

Cochran



	0150
	Minnegasco
	They increased their nom at Grundy by 39,000.

Coash




slb  

