[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Tues., Feb. 5, 2002  (Munson, Welsh, Calhoun, Cummings)

	0710
	Red Cedar LaPlata
	I received a call from Kim with Red Cedar to say that the LaPlata point may be coming in short today between 2-4 million short.  They have a compressor that’s going to be down in the field for 4-6 hours.  I passed the information on to Darrell.

Munson



	0830
	LaMaquina
	WFS LaMaquina is coming back up to rate.  They’ve got their problems taken care of at the plant.  CO2 level is back down within spec.  I touched base with Terry at their gas control.  He asked that we set the setpoint on nom.  I had shut them in earlier due to the high CO2.  I talked with Blackie.  He is on location.  He confirmed the CO2 is down.  I put them on their nom for the day.  It shows to be on the low side with the differential.  Blackie said it would be all right.

Munson



	0900
	Valero Ward
	We’re going to run Valero Ward about 14 million short today.  This is because we overflowed to them yesterday.  I OK’d this with John at Valero and Darrell here in gas control.

Munson



	0940
	Lone Star Pecos
	Due to the drop in the nom at this location.  I’ve requested a plate change be made.  Robert Baker said he would take care of it.  I also touched base with Steve in Lone Star gas control and he thinks that’s a good idea also.  While I had Steve on the phone I confirmed that we will be batching the Lone Star Ward point a little bit later this evening.

Munson



	0945
	Citizens Griffith
	I confirmed with Hugh at El Paso that they have a nom there of 5 million.  We are going to open it up for 50 until we accum the 5 just like we did yesterday.

Munson



	1003
	NWPL LaPlata
	The LaPlata flow just went to zero at NWPL.  I talked to Vi at NWPL gas control.  She said they are having some problems.  They hope to have it fixed very quickly.  The flow should recover.  I let Terry know at our LaPlata station.

Munson



	1005
	Canadian River
	We’ve got some HP down at the Canadian River station.  I informed Chris on that team.  He said he or one of his teammates would take care of it.

Munson



	1030
	Canadian River
	Mike Flynn has units 1 and 3 back on line.

Munson



	1030
	
	The NWPL flow at Ignacio LaPlata has recovered.

Munson



	1125
	WFS Milagro
	The flow rate at WFS Milagro has dropped off.  It’s running about 25 million short right now.  I called Terry at WFS.  He said that he would call the plant and take care of it.

Munson



	1310
	PNM Wingate
	I asked Mike Boatman to check into the control functions on the PNM Wingate station.  The night shift had a problem with the station opening up past the control setpoint.  PNM complained about getting too much gas.  Our night crew immediately shut the station in.  I requested that Mike check into it to see if he can find out what might have happened last night that caused it to open up.

Munson



	1340
	WFS
	I called and talked to Mike at WFS.  Went over numbers with them.  I told him I show he is a little behind for the day.  He agreed.  He said he will try to pick the pace up at LaMaquina and Milagro.  Right now he said he has some supply that is not coming in up there due to some HP being down.  As soon as it gets back he’ll be able to increase the flow rate to us.

Munson



	0745
	Owatonna
	Put the unit on because our pressures out west of Farmington going out towards Willmar were getting low.  Also we were low going north to Farmington.

Calhoun



	0745
	Beatrice
	They shut unit #19 down on the “C” line.  That allowed the gas to free flow up the “B” line.  They were able to save fuel by taking the unit down.

Calhoun



	0907
	Medford
	They took their withdraw rate from 50 to 10.

Calhoun



	0910
	Viking Chisago
	We had a nom of 3.9 to them.  They were going to bring on Chisago at about a 14 million rate and batch it.

Calhoun



	1025
	Farmington
	Shut #6 down.  It was on the “A” to “BC” pulling the Medford gas in.

Calhoun



	1125
	NBPL Ventura
	Reduced the rate from 725 to 700 to come in for the rate for the new gas day.

Calhoun



	1315
	Owatonna
	Shut the turbine down.  The loads had backed off and our pressures were back in good shape.

Calhoun



	1355
	Farmington
	Shut unit #5 down.  We were in good shape going north of Farmington.

Calhoun



	1440
	Alexandria
	Shut the unit down.

Calhoun



	1515
	Ventura
	Took unit #14 down.

Calhoun



	1520
	Ogden
	Shut #13 down going north.

Calhoun



	1530
	NWPL
	I noticed that the NWPL flow at LaPlata dropped off again significantly.  I called Vi and she said that they had people working on their measurement equipment out there and evidently something that they were doing caused the flow to become erratic.  She apologized and said that the flow should be recovering very shortly.  I notified Larry at the LaPlata compressor.

Munson



	1540
	Oakland
	Had them drop one unit on the “BC” and also one of the verticals on the “D”.  We were starting to pack up at Ogden.

Calhoun



	1600
	Hubbard
	Shut the unit down.  Called Corn Belt before I did.

Calhoun



	1605
	Carlsbad
	We have a low voltage alarm coming in from the Santa Fe Bilbrey location.  I notified Randy on the Carlsbad team.

Munson



	1630
	WT1
	While making a two for three unit swap at WT1 they lost units 2 and 3.  They are both down at this time.  The only unit on right now is unit 1 but it’s throttled way back into idle position.  There is personnel on site trying to get everything back on.

Munson



	1710
	Crawford
	Unit #1 has gone down due to the problems at WT1.  I notified Randy at WT1.  He said he would get someone on it.

Munson



	1615
	Minnegasco
	They did a backhaul.  They wanted to reduce their withdrawal rate at Glenwood from 14 and took it to zero.  Also Trailblazer, they took a 21.742 to zero there.  We contacted NGPL and we made those things happen.

Calhoun



	1630
	Redfield
	Talked to Steve Thomas.  They were wanting to get Redfield withdrawal rate cut back to 300.  I called the Redfield station and talked to Gary.  He was going to make that happen.

Calhoun



	1730
	Ogden
	Shut unit #17 down.

Calhoun




 1830 to 0630 Shift Tues., Feb. 5, 2002  (Hardy, Armitage, Spain, Muntz)

	1816
	Monahans Team
	I notified Rick Youngs that we have a low battery voltage showing up at the Sid Richardson block 16 fuel meter.

Munson



	1925
	Platteville
	I had a low battery voltage come in for Union Center.  I called and spoke to Lenny.  He was working on software out there today.  We just needed to change some new register numbers around for the battery voltage.  Ken Poole fixed it for us so everything is all right now.

Spain



	2000
	Ogden
	I took unit #13 off of the Redfield suction.  We had three units on there.  Looks like we only require two units to pull the 300 in from Redfield. The make up valve 90 was open quite a bit, about 45%.  I took 13 down and we really haven’t backed into Redfield but about 10#.   I called Redfield before I did that, spoke to Gary.  It was all right with him.

Spain



	2100
	Oakland
	I just called and gave Jeff and order to bypass the “BC” station at Oakland.  We’re cut back to a minimal amount of units there.  We still have 780 on the discharge side. Going to go ahead and let it roll back into Palmyra.

Spain



	2145
	Farmington
	Unit #2 went down.  It was on the Willmar service.  I don’t need it back on right now but I do need it available towards morning.  I called the on call person, spoke to Steve Smith.  He is supposed to try to reset it with his laptop and give me a call back.

Spain



	2330
	Palmyra
	I called Cramer out on unit #26.  It had an alarm on it for about ½ hour, wouldn’t clear.  He went out.  Informed me it was real foggy out there.  The air inlet filter to the turbine was probably frosting up a little.  He was just going to reset it so it wouldn’t go off again.  It will show in alarm here the rest of the night.  I’ll just have to keep an eye on it.

Spain



	0035
	Atoka 2
	Unit 837 is down. Armando is going to go check on it and restart it.

Muntz



	0100
	Farmington
	I put unit #2 back on Willmar service.

Spain



	0113
	Station 7
	Brett is bringing station 7 on line.  Need to pull gas away from station 9.  Currently have 1004 discharge down at 9.

Muntz



	0110
	Ogden
	Put unit #14 on going from the “BC” suction to the east discharge.

Spain



	0200
	Owatonna
	I started the Owatonna unit.  It looks like our zone E pack stayed about 1020 for the last couple of hours, since midnight.  Trying to get it to grow up to around 1050 for zone EF.

Spain



	0253
	WFS Milagro
	WFS control called and requested we cut the setpoint at Milagro back from 310 to a 300.  They had lost a big compressor.  He said that it would be about 45 minutes to an hour before they got the unit back on.  When they get it back on they’ll give me a call and have me increase the rate again.

Muntz



	0300
	Hubbard
	I started the unit at Hubbard.  I’ve got about 525 for pressure on the suction side of Earlville.

Spain



	0340
	Sublette
	Unit 14 is down.  Steve Showers is on his way out.

Hardy



	0338
	Station 7
	Unit 703 is on the line.

Muntz



	0455
	Ogden
	Unit #16 died.  I couldn’t get it reset.  It was on the Redfield service.  I put unit #13 on in its place.

Spain



	0500
	Beaver
	Have requested Beaver go to 725 on the “KB” line to pressure it up enough so we can bring gas south.

Armitage




slb  

