[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Tues., March 19, 2002  ()

	0905
	Humboldt IA TBS
	Got a battery voltage alarm, down to a 10.3.  I called the OCC and they got a hold of the on call field person for Ogden.  She said she would pass it on to the technician that takes care of that point.

Hall



	0904
	Sid Richardson
	Sid Richardson soured up, our valve shut in.  Keystone I’m showing the unit also went down.  At this time I called the OCC and requested the on call.

Barry



	1000
	Pipestone
	Called the OCC and they got a hold of the on call there at Harrisburg.  He said that he would get a hold of Lance and have him take care of the station flow and temperature.  It’s down to 2.3 degrees.  He also indicated that there is a problem at Fremont and Kenton with the scans.  He said he would take care of those.

Hall



	1100
	ANR
	Called and talked to Steve about Janesville.  He said they lost their compression.  They’ve got a guy out there.  He thought it would be right back up but it’s not yet.

Hall



	1245
	St. Paul 1Q
	Called the OCC.  They got a hold of Tony the on call person.  He got a hold of Tim who takes care of the St. Paul 1Q.  Tim had been out there yesterday but for some reason on the pressures, one pressure went to zero about 9:00, the inlet pressure has gone to zero about noon.  Tim will swing by there and take a look at it again and see what has gone wrong with it now.

Hall



	1306
	Humboldt
	Just got a call from the technician out there from Harrisburg.  He’s gotten it fixed.  He said there was a problem out there.  He said evidently a squirrel or something had gotten into the equipment and kind of messed it out but he’s gotten it taken care of and we’re back to showing 12.6 on the battery voltage.  Everything is looking good.

Hall



	1410
	St. Paul 1Q
	Just got a call from Tim.  He just replaced a communication board and the analog board out there.  He said he hopes that it lasts more than a couple of days because he doesn’t have anymore spare boards right now.  He has sent several in for repairs but doesn’t have any back yet.  Anyhow he’s got it working for now.

Hall



	1513
	
	Received a station alarm at station 9.  Called the OCC and requested the on call.

Barry



	1704
	Plains
	Louis is finished with the maintenance at Plains and we have the unit back on the line.  It’s back in remote.

Muntz




1830 to 0630 Shift Tues., March 19, 2002  (Moore, Alvarado, Barnes, Cochran, Coash)

	1915
	LaPlata
	Got up over MAOP there.  The discharge pressure at LaPlata hit 1012.  I started trying to cut gas at Ignacio and NWPL.  It did get up 1015, time frame of maybe about 10 minutes at the most.  It appears that we’re taking extra gas from WFS Ignacio to help them out, they’re doing some testing.  I made a call over there and talked to Ron.  I told him I would have to cut their gas some because of my pressure.  He said it would be over in about another 20 minutes.  I cut him 10 anyway to relieve pressure.  He said he would give me a call as soon as he gets the call that they’re finished with their emissions test.  Then we will cut them back about another 10-15, get them on rate there.  David is headed out to LaPlata because I did receive a station alarm there.

Moore



	1945
	LaPlata
	The discharge again has jumped up.  I’m showing about 1016.  It lasted between 5-8 minutes.  David is on site.  I did cut WFS another 10 and NWPL by 5 to relieve the pressures.  He has the alarms cleared and the unit is slowing back down.

Moore



	2030
	Lyons 
	Flow rate has erratic reading from measurement in the field.  Bushton can see a steady flow rate of 11.  At this time I have inhibited an 11 flow rate on the system.

Barnes



	2150
	Citizens Griffith
	I put a zero setpoint in that flow rate due to I’m getting alarms in and out,  block valves opening and closing.  In scanning the history it looks like it has been doing that for awhile.  I made a call out and talked to Trace over at Griffith to make sure that they are not taking any gas.  He said they aren’t taking anything at all.  There is a possibility that he may take a trickle later for the boilers but he’s not even sure about that.  I let him know that I was going to put a zero in there.  He didn’t have a problem with that.  He did say that he would call me if he starts to take anything off the line.  Again, I just did this to get that valve to stop opening and shutting.

Moore



	2156
	Hugoton
	Unit 9 down.  The on call operator Ken received a pager alert and will check on the problem.

Barnes



	2209
	Western Gas
	Benedum – Their flow went to zero.  I did call their plant and left a message advising them that they had only accumed 4.3 on an 8 million order.  I asked if they were having problems; it would be fine but that they needed to get the gas back on after they resolved their problems because they had only accumed the 4.3 on the 8.  I left a phone number on the answering machine and I’m waiting to hear from them.

Alvarado



	2219
	Stevens Co. 2
	Unit 11 down.  Mike the on call operator is on his way.

Barnes



	2250
	Hugoton
	Unit 7 on in place of unit 9 which has hot compressor valves.  It will stay down for the night.

Barnes



	2325
	Meridian
	The CO2 there has come up to 2.03.  Made a call out there and talked with Ben.  He said they are aware of it and they’ve already cut some bypass gas.  We should see it come back down in the next scan or two.

Moore



	0015
	El Paso 30” 
	I contacted El Paso gas control and spoke with Chapa.  I advised him that I was showing a 21.5 nom there.  They’ve only accumed at this time about 4.5 MMBtu rate.  He advised me that they were having problems with their HP and that they were trying to get other HP up and running so they could make the delivery to us.

Alvarado



	0155
	Bloomfield
	Made a call there and talked to Mary.  The CO2 is up again, showing 2.1.  She said she would cut gas and get that down.

Moore



	2335
	Stevens 2
	Unit 11 back on.

Barnes



	0034
	Stevens Co. 2
	Unit 7 on.

Barnes



	0059
	Stevens Co. 2
	Unit 10 on.  Units 7 and 10 units were added due to available field gas pressures.

Barnes



	0204
	Cunningham
	Requested Breeze to add a dual fuel unit to the three electrics that are already on.

Barnes



	0230
	Red Cedar
	Made a call over there to let them know I’m showing about 2.9 on the CO2 at this time.  He said they had a little spike.  We should see that come back down.

Moore



	0222
	Bushton Station
	Requested a recip unit on the “D” to “E” line.

Barnes



	0300
	
	Cunningham unit on.

Barnes



	0307
	Bushton
	Unit 26 on as requested.

Barnes



	0333
	Sublette
	Unit 14 down.

Barnes



	0340
	Sublette
	Unit 27 down.  Advised the on call Steve Showers.  I also advised Mullinville, Holcomb and Hugoton on call.

Barnes



	0427
	Sublette
	Unit 14 back on.  It went down on freezing in the air intake filter due to fog, moisture and low temperatures.

Barnes



	0449
	Sublette
	Unit 26 on in place of 27 that went down.  They are going to have to troubleshoot the problem on unit 27 this morning.

Barnes



	0530
	Dominion Tu__ Lake
	Earlier last night received a DC volt alarm about midnight.  I did call out and talk to Omer.  He said he would check it first thing this morning.  The alarm did clear about 3:00 this morning but it went back into alarm.  He is going to go there first thing.

Moore




slb


