[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Sat., Feb. 23, 2002  (Calhoun, Davis, Cummings, Armitage, Munson)

	0905
	WT2
	Darrel Mason has the #3 unit on as requested earlier at WT2.  We’ve had some increases in West Texas today.  It’s going to require some extra HP at WT2.

Munson



	0905
	
	John Ragsdale has the second unit on at Keystone to accommodate the increase on the Sid Richardson flow.

Munson



	1020
	Valverde
	I called Larry at the Valverde plant and asked him to bring the CO2 back down within spec.  He said he’s having some trouble with some of the trains due to El Paso swinging on them.  He will try to get the CO2 down as soon as possible.

Munson



	0615
	North Branch
	Shut unit #4 down.  That was so we can make room for higher noms coming in at Great Lakes for the day.  They were raising it from 165 up to 230.

Calhoun



	0640
	
	Minnegasco called in and said they were going to take Medford from 10 million withdrawal down to zero.

Calhoun



	0830
	Ogden
	Shut unit #17 down.  We were stacked up out east and also stacked up north and headed into a warmer day.

Calhoun



	0920
	Madison
	They wanted to take their nom from 60 to a 40.

Calhoun



	0900
	Waterloo
	Shut unit #2 down.

Calhoun



	0950
	Waterloo
	Shut #1 down.  We were still stacked up out east.  NIGas backed off 30 million for the new day.  They went from 190 to 160 and also Quad Cities and some of the other TBS’s were backing off.

Calhoun



	1000
	Farmington
	Shut unit #1 down.  It was pumping on the “BC” north.  The load had died off.

Calhoun



	1055
	Guthrie Center
	Shut the turbine down.  We were backing off and suctions were starting to come up at Ogden.

Calhoun



	1107
	Waterloo
	Shut unit #4 down.  I was still trying to back off of the east.  We were up on MAOP at Galena and the suction pressure is still coming up and we had Earlville down on bottom.
Calhoun



	1115
	Ventura
	Called the on call person to see if we could get someone to go out and shut down one of their verticals.

Calhoun



	1130
	Waterloo
	I did a station stop and finished shutting down the remaining HP that was on, units 3 and 5, and bypassed the station.  That’s because the load had died off out on the east leg and also we were going to leave Hubbard on to get some more run time on it.

Calhoun



	1500
	Oakland
	Had them bypass the “D” station.  The loads had backed off in the market area and we were packing up real fast.

Calhoun



	1520
	Minnegasco
	They called in and was wanting to do a 40 million backhaul to Glenwood.  We already had a 20 million nom there so that made a total of 60 million.  We ran it through the calc sheet and it looks like we’re going to have to run 75 for the remainder of the day to come in on rate.

Calhoun



	1530
	Ogden
	Shut unit #16 down on the “BC” going east.  We were still stacking up and had to get off of the east leg some more.

Calhoun



	1151
	Brownfield
	Put the turbine on line due to pressures in the 30” above Spraberry and not getting El Paso in on the 30”.

Armitage



	1640
	Zia Plant
	The Zia plant flow went down approx. two hours ago.  Tried calling the Conoco plant to get an update on how much longer it might be down.  They’ve been able to pick up most of the gas through Conoco but there is a small amount that is going out of balance.  I left a message at the Conoco plant for a call back.

Munson



	1710
	Beatrice
	Took unit #27 down.

Calhoun



	1735
	P1
	The unit at P1 just went down.  I notified James Fogg through the OCC.

Munson




 1830 to 0630 Shift Sat., Feb. 23, 2002  (Hardy, Henley, Spain, Muntz)

	1910
	Burdett
	Dennis called.  He and Floyd have got units 1 and 6 back up.  They think it was the gas detection in the basement there that set everything off.  They reset it to make sure it doesn’t happen again.  Everything looks good out there.  I called Larry with the Holcomb pipeline team to let him know.  He was concerned because BMG called him because they weren’t able to pump into us.  Their unit is down.  They will be bringing it back on tomorrow.  They are not going to send anybody out tonight.  They are only pumping about 1 million to us.  I also called the Holcomb operator to let him know.

Hardy



	1952
	Station 1
	I’m bypassing the station due to no demand.  Griffith is going to go down tonight and I have about 980# at Needles.  I’ve taken unit #2 down already and working on unit #3.  I talked with Baxter.  He’s going to go out and check everything out.

Henley



	1952
	P1
	The unit is back up and running.

Henley



	2110
	Minnegasco
	McCray called in.  He wanted to turn back another 40,000.  That will mean we need to run about 115.5 total up to Glenwood.  It’s including the previous 40,000 this afternoon.

Spain



	2144
	
	Just spoke with Blackie from Bloomfield.  He had been working on the Red Cedar receipt point and also the WFS Ignacio and LaPlata Red Cedar.  The CO2 and some of the other Chromatograph readings were locked up due to a programming error, but he had downloaded a new program on Thursday afternoon.  Those are all working correctly now.

Henley



	0010
	Cunningham
	I called and asked the operator to take us to about 200 million injection.  Central line pack has grown about 60 million in the last six hours.  We’re also getting an additional 200 million from the south that wasn’t anticipated in the plan.  The operator is going to check everything out to see if he can do it himself or if not he will have to call someone out to help him.  They’ve got a tower open for withdrawal that they can’t close to turn around to injection.  He’s not able to do it on his own.  He’s going to get some help out.

Hardy



	0130
	Beaver
	Randy sped up at Beaver.  Pulled the “KB” down to 628.  Trying to pull more gas through Plainview.  Currently have 337 going through Plainview.  Brownfield sped up where I’ve got 396 coming through Brownfield.  At Shell Tippet they called and needed to dump an extra 25 million over on us.  The nom was 18 million.  He said that Oasis was full and they had no place to go with the gas.  I advised him that we were getting full over around Spraberry and if he could make some room somewhere else we could help him out for a short while but he’d need to cut back early this morning.

Muntz



	0145
	North Branch
	I got an alarm in here for the Anoka TBS on the gas temperature.  It started going down about midnight.  It’s been trending down, it’s 1.3 degrees now.  The heater must have gone out at the TBS.  I called the on call person, spoke to Greg Lindblom.  He said he would go out in the morning and relight it.

Spain



	0215
	Citizens Griffith
	It is down until Monday.

Henley



	0301
	Beaver
	Just spoke with Randy and asked him to put another 2000 on to pull gas away from the south and lower the “KB” pressure down to 600.  Currently running about 625.

Muntz



	0332
	Ellis Co. 3
	Unit #6 just shut down.  Bill Foresman is going to go out and restart it.

Muntz



	0330
	Sublette
	Unit 21 is off line.  Called and talked to Rick Titus.  He’s going to call Oneok to see if they lost anything and then go out to the station and check everything out.

Hardy



	0345
	Plainview
	Just spoke with Andrew.  He is going to go try to bring Plainview on pumping north.  Currently we’re free flowing about 347 through Plainview.  That’s about maxed out for what we can free flow.  Still need to get the gas off of Brownfield so it won’t be in surge.  Andrew said he would call me when he got the unit up and going.

Muntz



	0440
	Plainview
	Andrew has the unit on the line at this time.

Muntz




slb  

