[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Sun., Dec. 30, 2001  ()

	0730
	Macksville
	Got a hold of the Macksville operator and requested the third turbine be put on.  He is headed to the station now to get it warmed up and get it ready to go on line.

Armitage



	0700
	Tate
	Have lost unit 4 at Tate.  Trying to get a hold of the Tate operator now to send him to the station to get it back on line.

Armitage



	1030
	Western Gas
	Benedum – It looks like their interconnect is down.  I called George over there at Benedum.  He said they have a unit down and they are having some problems.  They do have a mechanic there and they are going to let me know just as soon as they can if this is a long term thing or a short term thing.  He sounded like it might be short term.  I alerted my person at the Spraberry station, Ruben.  Told him that he would be losing about 30 million right off the bat.  He said that he will deal with that.  I’ll let him know just as soon as I know something.

Welsh



	1050
	Roger Mills

 Sandstone
	We had some measurement problems out there this morning.  It looked like it started in the wee hours of the night and probably around 0100 this morning that point started to flow the opposite direction.  We have every reason to believe it didn’t.  We talked to Transok.  Their pressure was a lot higher than ours.  We don’t see how it could have but the measurement indicates that it did so we don’t have true measurement.  We had Ken with the Roger Mills team, our on call person today go out to the point physically.  I did send a setpoint to shut it off.  He got out there and verified that it is shut off.  We got Transok’s gas control and Ken on a conference call with myself and we decided with the snow, the weather, dangerous conditions out there that it didn’t merit calling more people out there today and that since it’s only 10 million and we’re sort of believing that we may have gotten the 10 million from yesterday even though we can’t verify it with the measurement that we have.  It’s a matter of 20 million that is due to NNG and they can make that up and they agreed they would.  In light of that we left the point shut in today.  Monday when everybody is at work and they have extra help they will determine what the measurement was and get the problem fixed.

Welsh



	0625
	Madison
	They wanted to go from 43 to a 55.

Calhoun



	0830
	Terra Chemical
	Got a call from the plant manager.  He said they were going to be increasing their rate throughout the day from about 22 million up to about 36 where they normally run.  He said they should be there within 12-24 hours.

Calhoun



	0930
	Beatrice
	They went out and got unit #24 back available.  They put it on line and took #23 down.  Also they put unit #19 on.

Calhoun



	1020
	Ventura
	Jim called and said he was out at the station looking the units over.  Unit #11 had an oil leak. He said he was going to have to shut it down long enough to fix an oil line and it wouldn’t take more than about an hour.

Calhoun



	1120
	Ventura
	Jim got unit #11 back on line.

Calhoun



	1230
	NSP Viking
	Had an intraday nom come in for about 10 million at Chisago, receipt gas to us.  I talked to NSP and also Kathy Washington.  It does look like there is an imbalance out there where we owe them about 8.5 for the month, 12.5 cumulative, so we decided to leave it shut in to help to balance that point.

Calhoun



	1130
	Heartland Corn
	They increased their rate from 2.6 to 3.6.

Calhoun



	1335
	LS Power
	Whitewater – They called and said they were going to come on line.  They were going to come on line on a minimum load and pull until about 10:00 tonight.

Calhoun



	1335
	Waterloo
	Unit #8 went down.  I was able to reset it and got a clear.

Calhoun



	1435
	Beatrice
	Shut #22 down on the “D” line.  It was a 2000 HP unit.  They were out there earlier today and they had done some switching around.  They put on unit #19 which was a 2000 HP earlier.  Really didn’t need it because the “D” line was up on top and the other units were slowed down.

Calhoun



	1450
	Belleville
	Shut down units 1 and 2.  Our loads out east weren’t really high enough to have 1 and 2 running so I shut them down.  I’ll speed Galena up to make up the difference.

Calhoun



	
	NBPL
	I got a call from Loren.  He said they lost CS13. They got it back on at 1500.  He said it was up on exhaust temperature.  They were going to try to walk it up slowly so they didn’t knock it back down on exhaust temperature.

Calhoun



	
	Farmington
	Shut down unit #6 at 1530.

Calhoun




1830 to 0630 Shift Sun., Dec. 30, 2001  (Hardy, Henley, Spain, Monden, Muntz)

	1905
	Stevens Co. 6
	Unit #5 went down.  Stan is going out.

Spain



	2008
	Diesart(??) IA TBS
	It has a low battery voltage.  Called OCC ad they got a hold of Jeff Korey.  He said that their field team was aware of it and were on top of it.

Monden



	2315
	Tate
	I’m showing about three units down at Tate.  I called OCC. I spoke to Lonnie.  He is going out for us.

Spain



	0040
	Finney Co. 3
	Unit #3 went down.  Jay Harris is going to send someone out.

Spain



	0145
	Tate
	Lonnie called back in.  He’s got those units back on line.  He did have a freeze off on the panel going to unit 13.  It took him awhile to thaw that out.

Spain



	0205
	P3
	Unit 5 shut down.  Jerry is going to go check it out.

Muntz



	0220
	Finney Co. 3
	Dave Powers called back in.  He informed me that they have a freeze up on a controller out there on unit 2 that went down earlier when I called him out.  Actually I spoke to Jay Harris earlier and he called Dave Powers out.  They’re going to leave that unit down. They need a space heater run on the equipment out there.  Their policy is there needs to be two people present when the space heater is running so they are going to let it go until morning.

Spain



	0350
	P3
	Unit 5 is back on the line.

Muntz



	0355
	Warren Eunice
	They’ve got an H2S alarm of 3.1 out there.  Called and talked to the operator. He said they had a boiler shut down and they’ve lost everything out there.  They are working on getting it back on right now.  Right now the valve is shut from Warren Eunice and we’re not taking any gas from them at this time.

Hardy



	0357
	Red Cedar
	Scada is out at Red Cedar.  I had Roderick try to restart it from here.  He wasn’t able to.  I called out Terry and he is going to go see if it’s got snow on the dish and warm boot it, get the scada to come back in.

Muntz



	0400
	Sublette
	Unit #23 went down.  It was on the Haskell service.  Steve is going out.

Spain



	0230
	Cunningham
	I gave Linda an order to increase the withdrawal rate from 225 to 275.

Spain



	0434
	P3
	Unit 5 just went down again.  I paged Jerry.

Muntz



	0436
	Heartland Corn
	Pressure dropped below 300#  to a 298.  Called the plant and left a message that the pressure had dropped below 300.  Also coming out of Farmington down the Willmar line, it was discharging 927.  I did inform Steve January of this situation.

Monden



	0505
	Heartland Corn
	Someone did answer my call this time, Paul Ecker.  Informed him that the pressure was at 284.  They said they would take the appropriate action, when their downstream pressure got close to 60# then he would leave that decision up to his boiler man of when to go over to an alternate fuel.

Monden



	0515
	North Branch
	Unit #2 was put on line to pump down the Benson lateral.

Monden



	0525
	Koch Rosemont
	The RTU is communicating back to Houston.  Bob Tornio was out.

Monden



	0535
	North Branch
	Unit #2 went down.  Tried to start 4 and 1. They did not come on line or even seem to indicate a start.  Will leave it for the daylight operator to resolve.

Monden



	0547
	Heartland Corn
	Pressure is down to 255.  Spoke with Steve January.  He said they need to get it switched over to alternate fuel, one of their boilers.  I spoke with Paul Ecker at Heartland Corn.  He said they would get one of the boilers switched over to propane.  At this time Winthrop pressure is 238.

Monden




slb  

