[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Thurs., Jan. 31, 2002  (Cochran, Coash, Moore, Alvarado, Barnes)

	0613
	Canadian
	We have received AC power back.

Alvarado



	0618
	Station 5
	Unit 503 has gone down.  I have contacted the on call and advised them to go ahead and bring this unit back on.

Alvarado



	0618
	WFS LaMaquina
	The flow started acting up and causing some problems at their compressor station.  I started checking.  It looks like our control valve was sitting there jacking, it’s not holding a set rate.  I resent the setpoint.  It looks like it’s trying to control at this time.  I did notify the Bloomfield team. Walt is going to go out and check on this interconnect for us.  He said it’s going to take him awhile due to the weather.

Alvarado



	0712
	WFS LaMaquina
	Have made contact with WFS and they are saying that they have ESD’d at this interconnect.  The flow has gone to zero.  This is the same interconnect that we had problems earlier with.  I have not heard from our field personnel.  I believe that we were having some valve control problems but I don’t think that the ESD is due to our valve problem at this time.

Alvarado



	0635
	Gaines Co. X-over
	RTU hasn’t been communicating since 0425 this morning.  Advised Pat on the Andrews team.  He will ask Charlie May to go by and cycle the power on the RTU and see if that will bring it back into communication.

Barnes



	0715
	Llano Lea
	Spoke with their gas control.  They plan to have a lower flow to us for 4-6 hours during a hot tap this morning.

Barnes



	0803
	Station 8
	Unit 802 has been taken down.  This unit was brought on last night when they were having problems with the unit at station 7.  At this time there is no demand for this unit.

Alvarado



	0814
	WFS LaMaquina
	I just had a conference call with Brian our field personnel and Ron the WFS gas controller.  He’s saying that the ESD that happened at LaMaquina it is going to be about three hours before they can get the gas back to us.  We decided to let Brian and them go back to their station.  It’s only a 20-30 minute drive back over there.  Once they come on they can check our controller.  They think that our controller might be causing problems.

Alvarado



	0830
	Cunningham
	Asked Cunningham to go up to a 300 withdrawal.  Right now they’re doing 190.

Coash



	1000
	Sunflower
	They called and said they were going to come on for about a four hour test run with one unit.  I notified Oneok at Bushton Products.

Coash



	1029
	WT1
	Unit #3 has gone down.  I do have people on site and hopefully we’ll have this unit back on shortly.

Alvarado



	1019
	Gaines Co. X-over
	DAS back in service.  Charlie May discovered a battery voltage problem which he was able to correct.

Barnes



	1106
	Crawford
	I’ve lost unit 1.

Alvarado



	1127
	Maljamar
	I’m getting a station alarm, also an ESD test switch alarm and units down.  I have contacted the on call.

Alvarado



	1137
	WT1
	Unit 1 is back on.

Alvarado



	1145
	WT1
	Unit 2 is down and was brought back on at 1149.  We’re having unit problems at WT1 which is causing problems at Maljamar and Crawford.

Alvarado



	1230
	Redfield
	Just requested they go from 330 down to a 300 withdrawal.

Cochran



	1230
	Tescott
	Took #5 off the “E” line and cut Cunningham back to a 200 withdrawal.

Coash



	1240
	Minnegasco
	Just received a call from dispatch up there that they are going to take 18.889 back to Glenwood.  They are bringing back 48.567 at Grundy.  It’s not as cold and don’t have as much loads up there as they anticipated so they are bringing the gas back.

Cochran



	1400
	WFS LaMaquina
	It is flowing about 26.5 million back to us.  This interconnect has been down for quite awhile due to them having an ESD on their side of the system and also trying to get their units back on.

Alvarado



	1520
	Ogden
	I just dropped unit #13 going east, no demand.

Cochran



	1645
	Hubbard
	Just dropped the compressor station at this time.  I was told by Dan Wilson we were going to have a peak alert today so shut it down from 5:00 to 7:00 time period.

Cochran



	
	Note
	This is concerning the Continental “C” line water, POI 1309.  At Gary Spraggins request a test on the water content was done by Dennis Hall of the Beaver team using a dreager stick reading.  He assessed 14# of water.  This was around 1:00 this afternoon.  Just after that I called the Continental plant and spoke with Clayton the plant operator.  I told him that we needed to shut the gas in, that we could not take gas out of spec at this high of water content.  He would not shut the gas in.  He would only say that they’ll see what they can do with the water content.  Gary Spraggins when told it was 14# requested that it be shut in.  We then requested Dennis Hall to manually shut the valve so that we would not be taking the gas.  However the shut in valve at the meter run is in Continental’s plant yard.  It’s their meter run and our meter.  Thus we could not manually shut it in.  At about 1430 I spoke with the plant supervisor for Continental, Ronnie Ashlock.  He would return to the plant and do a water test with his instrument and our dreager stick tubes and try to get a comparison.  However he declined to go to the plant after being about halfway there and suggested that our people as in Dennis Hall would go in their plant and see their reading and pull a dreager. They did so finding 4# of water, agreeing on 4# of water so it was not shut in.

Barnes



	1620
	El Paso Dumas
	POI 186 – NNG temperature probe is reading –43 degrees causing a discrepancy with El Paso.  El Paso’s custody transfer meter, the pay meter, NNG records a 59.4 rate while El Paso measures 52.  Advised Sunray to replace this probe which is used for volume calculation.  They said they would turn it in to their measurement tech who is at this time off due to a death in the family.

Barnes



	1730
	Alexandria
	Just shut the unit down, no demand.

Cochran



	1719
	Beaver Co. 1
	AC power back on.  Advised Rick Preisner.  An operator will be dispatched to restart the units.

Barnes




 1830 to 0630 Shift Thurs., Jan. 31, 2002  (Munson, Cummings, Welsh, Calhoun)

	1833
	
	Delhi Beaver is still flowing.  They had run it a couple of days ago to bring in a pig and had strattled two days already. I called and asked why they were still on.  They said the storm has made it to where they can’t get out there and do anything with it.  So I’m just going to let them flow tonight because of the ice storm in the Beaver area.

Cummings



	1804
	Valverde
	I noticed a high CO2 level at Valverde.  I called Mary at the plant and asked her to get that back within tariff.  She said that she is having trouble with train #5 and she has already taken action to bring the CO2 back into spec.

Munson



	1845
	LaPlata
	We just had a severe spike in the discharge pressure at LaPlata.  I did a demand scan and the very next scan it went immediately back down to a more acceptable level.  I’m not sure if this was a glitch or if we have a real problem.  It did indeed trigger a station alarm along with the spike.  I notified David through the OCC.  He’s on his way back out there even though everything looks OK at this time at LaPlata.  It was just a one scan spike but he is going to go check things out.

Munson



	1845
	Station 7
	We lost unit 703 and I notified the OCC.

Munson



	1901
	Station 7
	The OCC put me in contact with Brett.  I made him aware that he has a unit down and I need it back on as soon as possible.  If he’s not able to get it on I asked him to let me know so I could go to station 8 similar to the action we took last night.

Munson



	1909
	LaPlata
	David is on site at LaPlata.  He found everything to be functioning OK at this time.  I did send him an e-mail with the data on the discharge pressure spiking so he can look at it.  I also sent him data for the flow rate on the WFS Ignacio flow so he can compare that to his records.  He cleared the alarm and will be leaving the site shortly.

Munson



	1914
	Station 7
	Unit 703 is back up.  It went down on the seal oil trap failure problem that we had last night.

Munson



	2348
	Stevens Co. 4
	Unit 4 down – Paul with the Stevens Co. team is on his way to check it out.

Welsh



	0002
	
	I’ve been talking to Clifton’s team leader, Hank.  He’s been working on unit 31.  It seems like we can’t get our signals together on the check backs and the setpoints.  He’s been out there quite a bit this evening working that.  We can’t seem to find the problem unless the satellite dish has got ice on it or such.  We went ahead and reset the setpoints and we’ve got the engine set where we need it.  We’ll just let it go from there and try it.  We are going to have some technicians look at it in the morning from here and from Clifton.  We did use Hank’s help a lot this evening.  He’s been out there twice since about 6:00 tonight trying to get the signals to work.  We think we’ve got it working as best we can.

Welsh



	2348
	Stevens Co. 4
	Unit 4 – We had a change of plans on that.  Paul with the Stevens teams decided to leave that unit down.  It went down on low suction.  They are going to wait until first thing in the morning to go out and start that unit.

Welsh



	1800
	Ventura
	Unit #12 went down. I called the on call person.  Jim was going out to see what it went down on.

Calhoun



	2015
	Ventura
	Jim said they found a bearing sensor that had gone out.  They replaced it and got the unit back on.

Calhoun



	2035
	Ogden
	Closed valve 91 which split the “D” out from the “BC” suctions.

Calhoun



	2100
	LS Power Whitewater
	They called in and said they were going to be shutting down for the evening and they’d be back on about 5:00 in the morning.

Calhoun 



	2145
	Oakland
	Called the on call person Jeff.  He was going out to bypass the “D” line.

Calhoun



	2240
	Ogden
	Shut down unit #15.  It was on the “BC” going east and was cracking north.  I was trying to get off of the north end so I shut it down.

Calhoun



	0005
	Owatonna
	Shut the unit down.  I was recycling about 64% and I was still needing to get off of Farmington.

Calhoun



	0136
	Red Cedar
	The CO2 level at Red Cedar is running slightly high.  It’s just a little bit over 3.0 at this time.  I did touch base with James at the Red Cedar plant.  He said they’re having some trouble trying to get things lined out.  He expects the CO2 level to drop back to spec very shortly.

Munson



	0230
	Sublette
	They had a low ESD pressure.  Bill Lowe is going to go out and take a look at it.  It’s right on the border.  It’s probably within 1# of setting off the first low alarm.  He is going to go out and take a look at it.  It’s been steadily dropping to that level all evening.  He feels the need to go look at it.

Welsh



	0230
	
	We asked Cunningham to go to 350 withdrawal.  Gloria is diligently working on that.

Welsh



	0215
	WFS
	I noticed that WFS is running behind now on their rates for today.  They seem to have lost some of their supply at Milagro.  I talked to Terry at WFS.  He say they did indeed lose some supply and he’s not going to be able to get it back at Milagro.  He told me I can pick up a little bit at Ignacio and LaMaquina but he said he’s not going to have enough to make rate for the day.

Munson



	0245
	Station 7
	Unit 703 is down.  I notified Brett at the location.

Munson



	0300
	Gallup
	We have a unit alarm at the Gallup compressor station.  I informed Mike Boatman through the OCC.  Mike is going to go out and look things over.  It’s most likely caused by a dip in the surge margin but he will check things out.

Munson



	0312
	Red Cedar
	Red Cedar is still running above spec on CO2.  I called them again.  This time I talked to Randy.  I asked him to bring their CO2 back down to 2.8 or less.  They told me that they would see what they could do.

Munson



	0258
	Stevens Co. 6
	Unit 5 is down.  They opted to leave that down until sun up.  They said it’s probably low suction.  They will go out and start it first thing this morning.

Welsh



	0335
	Station 7
	Unit 703 is back up.

Munson



	0451
	
	Concerning the Rolla, KS TBS #1.  We have a low station battery voltage.  We called Joy from that team. She said it’s most likely a solar power deal where it didn’t charge up.  The extreme cold weather is hard on that battery but she will run out there and look at it first chance she gets.

Welsh



	0500
	LS Power Whitewater
	They bought a unit on line.

Calhoun



	0535
	NBPL
	They called and said that CC was ready to start testing at the interconnect.

Calhoun



	0535
	Alexandria
	Put the unit on line.  Benson was starting to fall off.

Calhoun




slb  

