[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Mon., Feb. 25, 2002  (Moore, Alvarado, Barnes, Coash)

	0638
	Red Cedar
	CO2 there has come up to 3.36.  Made a call over and talked to Jack.  He said that it should be on the way back down.  They are working on the problem.  They had lost a couple of units there.

Moore



	0615
	Stevens Co. 6
	The station is now back on line.  They had a partial ESD earlier.

Barnes



	0745
	Ventura
	Talked to Jim.  He’s going to put some units on the “C” line.

Coash



	0800
	Harrisburg
	They opened the valve that they’re holding back pressure with towards Aberdeen since we’ve got some colder weather coming in the next day or two.

Coash



	0740
	Clifton
	Requested unit 30 on “CD” suction to “CD” discharge.

Barnes



	0745
	Cunningham
	Requested Breeze to withdraw 300. At present they are shut in.

Barnes



	0756
	Macksville
	Requested two units on.  I spoke with Bill.

Barnes



	0833
	Clifton
	Unit 30 on by remote start.

Barnes



	0833
	Bushton
	Requested unit 32 on as soon as we can get some gas their way.

Barnes



	0849
	Macksville
	Units 2 and 3 on as requested.

Barnes



	0850
	
	Lyons station to cut back flow for some minor maintenance.  The flow cut back from 19 to 12 for the next 2-3 hours.

Barnes



	0900
	El Paso Waha
	El Paso has called and asked if we could keep that 16 nom that they’ve got nominated for today at El Paso Waha.  I spoke with Gary Spraggins.  They had a nom of 5.  It looks like we’re going to accum about 15 so we’re actually going to end up only having to take about 6 million into our system for today.  Gary said that’s fine, we’ll just keep it and put it towards our imbalance.

Alvarado



	0942
	Plainview
	The unit at Plainview has been taken down.  No demand for this unit at this time.

Alvarado



	0945
	PG&E Topock
	Received a call from Rick.  He let me know that they have our control valve blocked open at this time because they are doing some work on their ESD system.  He will let me know when he’s finished.

Moore



	1052
	Bushton 
	Unit 32 on as requested.

Barnes



	1055
	Station 9
	Talked with Jesse out at 9.  They are going to swap some valves there to where station 9 will be pulling both from the mainline and West Texas, discharging up the Panhandle.  We’re doing this because we need more gas up the Panhandle lateral and to help relieve pressures on the mainline out west.

Moore



	11??
	
	…swapping units there.  He took unit 2 down and put unit 3 on line.  He’s got to change some hot valves on #2,

Moore



	1145
	Conoco Maljamar
	Received an alarm in here on the Maljamar station.  Looks like the units went down.  We lost flow from Conoco.  Made a call over there and talked to Randy.  He said they had a plant ESD.  It’s going to be down for awhile.  He’ll give me a call and let me know when he has an estimated time on starting back.  I did notify Randy on the WT1 team.

Moore



	1200
	Oakland
	They’re putting HP on the “BC” station.

Coash



	1230
	Conoco Maljamar
	Received a call from Ryan.  He let me know that they are ready to start gas back up.  I made a call out to WT1 and talked with Bennie.  He said someone was on their way out.

Moore



	1340
	Minnegasco
	They reduced their withdrawal at Trailblazer by 42,000.

Coash



	1400
	Finney Co. 3
	Low dehy alarm came in at 1138 this morning.  Advised the on call operator at 1400.  He was already aware of the alarm and plans to go by and check it.  However this dehy stands alone and they are experiencing a snowstorm with high winds.  Problems with this dehy is the wind will blow the fire out.

Barnes



	1415
	Station 1
	Earlier today Darrell Schoolcraft, Jerry Graves and myself talked to station 1.  Darrell gave them the OK to go ahead and block their mainline inside the yard.  They are blocking a section of the line for some work to be done.  We were flowing through the loop line going west.  About 1345 at station 2 and station 3 got up over MAOP.  We did see the pressures come up about 2# and then drop back off but around this time station 2 started climbing and continued to climb.  It did hit 1019 at station 2 and 1010 at station 3 before we were able to get the units down.  We did take units down at station 2, 3, and 4 to relieve the pressures.  We did notify Tiny about the pressures.  We may have had the high pressures for 10-15 minutes, between 1008 to 1019 at 2, 1007-1010 at station 3.  We are now in the process of getting some units back on.  I just got one unit back on at station 4 and we have one unit on at station 2 going west.

Moore



	1440
	Station 1
	Talked with Bo out there and Darrell Schoolcraft and Jerry Graves to come up with a new scenario they’re going to try at station 1 to pull that pressure down for the contractors.  We are going to put two units on line at station 1 to pull that pressure down and then we’ll take down the unit at station 2.  We’ll try and maintain our pressures like that.  Probably put on a second unit at station 4 and possibly a unit at station 3 later as needed.  I did notify station on what we were going to do and I will let them know as soon as we get units on line at station 1.

Moore



	1444
	Sublette
	Unit 21 has been down since 1352 because there is not enough gas from Oneok until they restart their unit.

Barnes



	1549
	Finney Co. 3
	Low dehy temp alarm, should clear soon.  The operator has bypassed the cooler and increased the pump speed.

Barnes



	1518
	Sublette
	Unit 21 back on.

Barnes



	1610
	Station 4
	I talked with Howard and asked him to go ahead and put a second unit on at station 4.

Moore



	1620
	Station 3
	I called and talked with JB there.  I asked him to go ahead and put a unit on line to pull away from 4.

Moore



	1613
	Finney Co. 3
	Low dehy temp alarm cleared.

Barnes



	1710
	Station 4
	We lost the second unit there.  Howard wasn’t able to keep it on.  It went down on discharge.

Moore



	1725
	Station 3
	Talked with JB.  We’re going to take that unit back down.  We’re over MAOP once again.  I’m showing 1014.  I told him to go ahead and take it down.  We had the unit on idling to try and pull away from 4 so we could get a unit on there but we hit the 1014.  It was only there for a couple of minutes.  We were over the 1008 for maybe 5 minutes.  So we’re going to take it down and let station 1 pull away for awhile before we attempt this again.

Moore



	1726
	Station 2
	Talked with Tracy.  We took that unit down there at 2. He’s going to open the bypass.  The one unit being on was causing more of a restriction than anything else.

Moore




1830 to 0630 Shift Mon., Feb. 25, 2002  (Hardy, Henley, Spain, Muntz)

	1930
	Atoka 1
	Unit 737 is down. Jerry is going to go out and take care of it for us.

Henley



	2205
	Hugoton
	Unit 14 is down. The operator on call is on his way.

Hardy



	2245
	Hugoton
	Ken called.  He’s got unit 14 back on line.

Hardy



	2245
	Stevens Co. 6
	The operator is out there on site bringing unit 1 back up for us.

Hardy



	2301
	Altura Gaines Co.
	I received a H2S analyzer malfunction alarm.  I contacted Frank Saragosa at Hobbs team.  He is going to go over and check it out.

Muntz



	2305
	GPM Linam
	I called and spoke with Tom at the GPM plant.  Their nom is currently is 83.7.  They are flowing 96.8.  I asked him if he could get back on nom. He’s beginning to pressure me up on the 26”.

Muntz



	2240
	Ventura
	Unit #11 went down.  I called the on call person.  Asked him to go out and check it out to see why it went down.  It might have water or oil or something running in the engine room.  I don’t need it back on right at this time.  I did advise him that we might be looking at putting it back on in the morning but for now I just need to check it out.  Rick is going out.

Spain



	0010
	Ventura
	Jim just called back in.  He has unit #11 back on line.  Trabon just skipped a beat there and knocked it down.  He thinks it will be all right.  I went ahead and shut the turbine down though.  Our differential was closing up.  The turbine doesn’t handle that very well.  It was just about to go into surge anyway.  I’ve got the three verticals on and the turbine down.

Spain



	0020
	Hugoton
	Ken called.  He’s got unit 14 back up and the station looks good.

Hardy



	0115
	Ogden
	I took unit #13 down.  Starting to pressure NBPL’s receipt out up there.  Need to cut some of that flow off.

Spain



	0145
	Brownfield
	I just spoke with Charlie May.  Asked him if he could put the Brownfield turbine back on.  Currently the suction at Kermit is up to 749.  I’ve got 750# at the crossover and still growing.  PowerTex only has 678# of pressure with 23 million going out.  It looks like I need to bring Brownfield on and close the block valve at Plainview and put the regulator in service back into Brownfield to keep differential.  This way we can pull the gas off of the crossover and also get the pressure boosted up for PowerTex and help get the pressure away from Spraberry.

Muntz



	0205
	Hugoton
	Unit 14 is down again.  Ken is on his way out.

Hardy



	0210
	Texas Co. 1
	Dee called in with a page on unit 2 going down.  He’s going out to the plant.

Hardy



	0250
	Crawford
	Lost the unit there.  It looks like the plant flow went to zero. Received an H2S alarm.  It looks like it closed down from there.  I notified OCC.  They are getting a hold of someone from the Carlsbad team.

Henley



	0305
	Crawford
	I just spoke with Bob from the Carlsbad team.  He’s heading out to the station.  Also spoke with Mike from Duke.  He said that he’s got somebody going out there too.

Henley



	0315
	Hubbard
	I bypassed the Hubbard station.  Need to back off the east leg.  I’m recycling a lot of gas at Galena.  Got 833 on the suction side, 960 on the discharge.  Also was anticipating the upcoming day.  NIGas nomination is going from 164 to an 88.  I did confirm that with the NIGas operator before I took the unit off.

Spain

 

	0323
	Beaver Co. 7
	Unit 1, unit 2 just went down.  Dennis Hall is going to take care of it.

Muntz



	0343
	Hugoton
	Ken called.  He’s got unit 14 back on line.

Hardy



	0403
	Woodward Co. 2
	Unit 1 is down.  Bill Foresman is going to go out and take care of it.

Muntz



	0405
	Spearman
	Unit 1 is down.  Bruce is going to go put it back on line.

Muntz



	0404
	Texas Co. 1
	Dee called.  He’s got units 1 and 2 back on line.  He’s still waiting on Oneok to put their units on to get him more suction so he can increase his flow.

Hardy



	0429
	Llano Lea
	Delmar H2S monitor malfunction alarm – Frank Saragosa is going to go check it out.

Muntz



	0445
	Ventura Interconnect
	Can’t get the “D” line north to respond to a setpoint.  I’m on MAOP on the “D” line.  I can’t seem to get off of it.  I’ve sent gas both south up the “B” and what it amounts to is the “D” line north regulator looks like it is stuck.  I called the Garner operator.  He is going to call someone for the interconnect and get them out there.

Spain



	0513
	Beaver Co. 7
	Unit 1, unit 2 are back to normal.

Muntz



	0514
	Spearman
	Unit 1 is back to normal.

Muntz



	0500
	Ventura Interconnect
	Mike called back from Garner.  He spoke to Dave Whitecotton.  Dave instructed us to send some big setpoint changes to the “D” line regulator and wait until it achieves it and then put it back to where you originally want the setpoint.  I’ve done that for about ½ hour now but the regulator is still is not reacting correctly.

Spain



	0517
	Woodward Co. 2
	Unit 1 is back on the line.

Muntz




slb  

