[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Mon., Feb. 11, 2002  (Hardy, Henley, Spain, Monden, Muntz)

	0640
	Station 7
	Unit 703 is on line and loaded.  Just spoke with Keith and he’s heading back to the house.

Henley



	0721
	Atoka 3
	Unit 842 is back on line.

Henley



	0732
	Owatonna
	At 0720 I sent a start command.  The unit loaded at 0731.

Monden



	0800
	Cunningham
	Talked to Linda.  We’re bringing withdrawal up from 100 to 300.

Hardy



	0800
	Station 5
	Unit 503 is on line.

Henley



	0910
	Station 8
	I just spoke with Mick.  He’s bypassing his fire detection for now due to welding in the yard.  We do have a station alarm on that.  He’s going to call when he is finished.

Henley



	0910
	Station 7
	Spoke with Norm earlier.  We received a station alarm there.  He’s going to clear it.  It looks like it is clearing now.

Henley



	0950
	El Paso Blanco
	I’ve been trying to slow down the rate there.  That flow control valve isn’t working properly.  I called El Paso and talked with Louie, one of the controllers.  He’s going to have somebody check that out.  That is their equipment, the RTU.  We just send the setpoint.

Henley



	1009
	Farmington
	Shut down unit #3.  The unit was slowed down and unloaded.  This is to see if one unit could sustain deliveries west.

Monden



	1009
	Beatrice
	Bob called and said they are having problems with the Trailblazer “B” line control valve.  They are checking into it.

Monden



	1022
	Trailblazer
	Spoke with Juan in their gas control to ask  him why their flow wasn’t up to 318.  Our pressure on that header is 582 and his pressure upstream is 711.  He said he had a 265 order and I have a nom of 318.  I called and spoke with James Carr.  He said he would call their scheduling people and talk with them to see if they had some problem if their system because the nom he had was the same as mine, a 318.

Monden



	1249
	Beatrice
	Bob called in and said they needed to work on the “B” line control valve that regulated the flow for the Trailblazer gas coming into the pipeline.  We’re going to take the gas all on the “D” line which we have four units on and have room to handle it on the discharge side, two 4000’s and two 2000’s.

Monden



	1343
	Skellytown
	Eric called and said they are working on the oxygen analyzer there.  He said we would be receiving several alarms and to disregard them.  He will call when they are finished.

Muntz



	1415
	Spraberry
	Tom is going to add another unit to the 24.  Valero Spraberry nom increased from 18 up to a 28.

Muntz



	1415
	Cunningham
	Brought withdrawal up from 300 to 425, the max.

Hardy



	1415
	Macksville
	I talked to Jim.  I asked him to put on two units for us pumping north to pull that gas out of Cunningham and to move more north.  Bart wants the north line pack up a little bit more to tonight.

Hardy



	1441
	Station 3
	Lost the whole station.  Contractor went out there and clipped a wire that knocked the station down.  They are in the process of putting everything back on line.

Henley



	1535
	Skellytown
	Eric called in.  He has finished calibrating on the O2 monitor at Skellytown.

Muntz



	1540
	Station 3
	Just spoke with Chris.  The station is back on line.  Everything is looking OK.

Henley



	1558
	Mitchell Plant
	The H2S has been holding around 0.25.  I called the plant and spoke with the operator out there.  Asked him if they had been having some problems.  Every once and awhile we spike up to 0.27.  He’s going to do some checking and get back with us.

Muntz



	1745
	Hugoton
	Unit 16 is down because of the fin fan going down and the unit over heated.  The operator is on the scene.  He’s going to restart the unit in about 10 minutes.

Hardy




 1830 to 0630 Shift Mon., Feb. 11, 2002  (Moore, Cochran, Barnes, Coash, Alvarado)

	1815
	Griffith Plant
	Received a call from Tom Tucker.  He let me know that he was finished with the equipment there.  He wants swap the gas flow to El Paso temporarily, probably 10-15 minutes.  They need to test run on the vibration at the full rate.  Again, this is temporary and then they are going to swap it back to us.  He’ll let me know when they are finished with that.

Moore



	1756
	Hugoton
	Unit 16 back on.  It was down due to a fin fan problem.

Barnes



	1755
	Sublette
	Unit 21 down.  Operator Rusty is in route.

Barnes



	1842
	Sublette
	Unit 21 is back on.  It went down on low suction due to low field pressure which has returned.  It was due to a field operator’s unit.

Barnes



	1902
	Hugoton
	Unit 16 down, the operator took it down.  He was getting a high temperature bearing reading.  They are going to have it down for a couple of hours to cool down and then replace the sensors and check it out again.

Barnes



	2000
	Cunningham
	Order changed for the withdrawal from 400 down to 200.

Barnes



	2142
	Hugoton
	Unit 16 – Bearing temperature sensors changed out and unit back on line.

Barnes



	2215
	Station 7
	Had Bill Lee the on call go out and slow that unit down, try to get it on the bottom, and he opened up the recycle some more.  I needed to back into station 9 some.

Moore



	2215
	Station 5
	I had Charlie go out and open up the recycle some there.

Moore



	2351
	ANR Red Deer
	We’ve been flowing an average of about 35 MMBtu at that point.  About 15 minutes ago the flow went to zero.  It stayed at zero for probably 10 minutes and then it came up.  I did make a call and talked to Mike on the Canadian team.  I let him know that at this time we still have a 35 setpoint in there and we’re flowing about 52.  We’re going to give it a little bit of time and see if that lines back out and gets on rate.

Moore



	0402
	Stevens Co. 4
	Unit 4 down on low suction of 19.5#.  The station operator will restart in the morning.

Barnes



	0457
	Hugoton
	Station alarm – Station operator also received a pager alarm and is in route.

Barnes



	0540
	Foley
	NSP called and said they were showing low gas temp.  I called Randy at North Branch.  He said they would take care of it.

Coash




slb  

