[image: image1.png]



          Services provided by Northern Natural Gas

          And Transwestern Pipeline Company

Enron Transportation Services
Gas Control Event Log

0630 to 1830 Shift Fri., Feb. 8, 2002  (Armitage, Hall, Barry, Braswell)

	0800
	Ventura
	Have made a phone call to Ventura compressor station requesting the verticals be put on going north on the “C” line.

Armitage



	0802
	
	Due to suction pressures falling and the east leg falling a little bit pressure-wise I’m starting Guthrie Center.

Armitage



	0805
	Palmyra
	Have raised the pressure on the “D” to “BC” to 700#.

Armitage



	0725
	Warren Eunice
	Lost flow there this morning. Called the operator.  Wasn’t able to get a hold of anyone.  I called the OCC for the on call for the Eunice plant.  Talked to Greg and he checked it out.  Everything seems to be OK at our plant, our part of it.  He said he was trying to get the operator as well and wasn’t able to get a hold of anybody right now.  He said they probably just shut us off for some reason.

Braswell



	0820
	Beaver Co. 7
	Received a call from Stanley out there.  He informed me that GPM will be running a pig this morning.  We may lose the units out there for time being.  He’s on top of it.  As soon as the water has cleared the line he will put the units back on at Beaver Co. 7.

Braswell



	0900
	
	Received a call from El Paso in reference to the El Paso Waha point.  They seem to think that the chromatograph is not updating out there and need someone to check that out.  Said it’s probably not updating since yesterday at noon.

Braswell



	0905
	El Paso Waha
	Talked to Rick at the Monahans team.  He informed me that they had been working on the chromatograph for about a week.  Don’t know why El Paso didn’t know that. That’s why it hasn’t been updating at that point.  They will get someone to look at it.  Apparently they are still working on the chromatograph.

Braswell



	1625
	Stevens Co. 2
	#6 is down.  The operator has called in.  He’s on the way to the station.

Armitage




 1830 to 0630 Shift Fri., Feb. 8, 2002  (Moore, Cochran, Barnes, Coash, Alvarado)

	1745
	PG&E Topock
	Keith called and asked if we could cut about 60 off of the flow rate for about three hours.  I asked them if half of that would do.  He said it would.  We were flowing about 265 so I cut to 235 for a few hours and then we’ll get back on rate.

Moore



	1746
	LaPlata
	Received a station alarm there.  Got a hold of the on call Terry and he is going to check it.

Moore



	1755
	Station 4
	Unit 403 – I received an alarm in here that the unit has gone down.  Robert is going to check it.

Moore



	1818
	Gallup
	Received a unit alarm there, probable due to the low surge.  All of this is due to the unit down at station 4 but he is getting that unit back up at this time.

Moore



	1940
	Skellytown
	Got a high oxygen reading. It’s presently reading .35.  I talked to the on call person at the location.  He said he would do some checking but he said there isn’t anything they can do about it.  He will get back with us.

Cochran



	1943
	Skellytown
	Just received a call back from personnel out there.  He said that they’ve got a problem at the Cargray plant and they are working on it at this time.  Hopefully they can get the oxygen problem resolved.

Cochran



	2140
	Skellytown
	Jerry just called in.  He said at the Cargray plant their de-ox unit is maxed out.  They’ve got more volume going through than what it can de-ox.  They are in the process of going out and throttling some wells back and shutting some gas back to try to get that within tolerances to bring the oxygen level down.  They are out there shutting gas in at this time.  They want to wait and see what things look like as we go towards morning as they reduce the flows and get within the capacity of the de-ox treater.

Cochran



	2150
	El Paso Blanco
	I made a call to El Paso to let them know we are behind on our delivery to them.  I’m showing a scheduled 336.9 on the Mcf and we’ve averaged about 322.  It looks like we’re going to be between 14-15 short.  I talked to Paul over there.  He said that their pressure is high and has been high today.  I guess Richard has tried to raise our pressure and make that delivery but we’re still having a hard time getting in there.  Paul did say that he is working on trying to get the pressure down.  I will try and raise my pressure some to make this delivery but it’s very possible we’re going to be short there.

Moore



	2150
	Stevens Co. 6
	Unit 1 went down at 2135.  I contacted OCC and spoke with Steve with that team.  He’s on his way out.  We’ve also lost Stevens Co. 6, unit 3.  I advised him on that as well.

Alvarado



	2151
	Clifton
	Unit 31 – We shut it down due to no demand.

Alvarado



	2229
	Finney Co. 2
	Received a station ESD, all units down.  I have contacted OCC.  Waiting to hear from the on call at this time.

Alvarado



	2335
	Stevens Co. 6
	Unit #1 is back on.

Alvarado



	0030
	Minnegasco
	Minnegasco raised their injection from zero to 60,000 at Glenwood.

Coash



	0143
	Station 7
	I received a station alarm there and malfunction alarm.  Got a hold of Keith through OCC.  He said that he was going to contact Norm.  Norm just called me back and he’s going to check that unit because I show a unit 3 alarm now.  I did let him know that the recycle valve is opening and shutting, and the torque is bouncing around.

Moore



	0221
	Atoka 1
	Unit 737 has gone down there.  Got a hold of Armando.  He’s on the way out.

Moore



	0430
	Atoka 1
	Unit 737 went down again.  Armando is on his way back out.

Moore



	0452
	P1
	Received a control panel station alarm there.  I talked with James Fogg.  He is going to go check it.

Moore



	0455
	GPM Zia Plant
	Flow went down to zero there.  Called out to Conoco Maljamar, talked with Ryan.  He said it is down.  I guess he just noticed that.  He will make a call out.

Moore




slb  

