TABLE OF CONTENTS












Page

1.0
 INTRODUCTION
1


2.0
PROJECT DESCRIPTION

2.1
Project Emissions
4


2.2
Netting Calculations
5


2.3
Alternative Operating Scenario Emissions
6

2.4
Ambient Air Modeling
7

2.5
BACT Analysis
7

3.0
AIR QUALITY REQUIREMENTS

3.1
National and State Ambient Air Quality Standards
9

3.2
Regulatory Summary
10

3.2.1
Federal Regulatory Requirements
10

3.2.2
State Regulatory Requirements
11

Appendix A
Tables

· Table 1
Proposed Turbine Emissions

· Table 2
Proposed Generator Engine Emissions

· Table 3
Netting Calculations

· Table 4
Alternative Operating Scenario Emissions

· Table 5
Station Emissions Summary

· Table 6
Example Calculations

Appendix B
Proposed Custom Fuel Monitoring Schedule

Appendix C
General Electric LM2500 Turbine Data

Appendix D
Area Map, Process Flow Diagram, and Plot Plan

Appendix E
AP-42 Data Tables for Turbines and Engines

Appendix F
Generator Engine Data

1.0
INTRODUCTION

Transwestern Pipeline Company (TWP) operates a natural gas compressor station (SIC code 4922) near Kingman, Arizona.  The facility is operating under ADEQ permit number 1000156, issued on April 16, 1998.  Existing equipment at this site includes three Ingersoll-Rand 616KVT gas-fired reciprocating engines rated at 4,000-hp and two 451-hp Waukesha LRZ3520GU generator engines.  These units were originally installed in 1966 and have never been modified.

The station, designated as the Kingman Compressor Station, is located in Mohave County approximately 40 miles east of Kingman, Arizona.  Mohave County is designated as an attainment area.  This application addresses the requirements specified by Arizona Revised Statutes (ARS).

TWP is currently in the planning stages of the Red Rock Expansion Project.  This project impacts four natural gas compressor stations located in northern Arizona.  The four stations are located near Kingman, Flagstaff, Leupp, and Klagetoh.  The project will result in the shutting down and abandonment of approximately 12,000-hp of reciprocating gas fired engines at each station.  These units are to be replaced with a single General Electric LM2500 gas turbine at each station.  This project will have a significant benefit to air quality through the reductions of criteria air pollutants from the stations.   

TWP is requesting air permits for this project from the ADEQ for the Kingman and Flagstaff stations.  The Leupp and Klagetoh stations are located on the Navajo Indian Reservation in Coconino and Navajo Counties.  TWP is currently seeking air permits for these two stations from the EPA Region 9 office. 

2.0 PROJECT DESCRIPTION

TWP is proposing to install a single gas-fired General Electric (GE) LM2500 gas turbine to replace the three gas-fired reciprocating compressor engines.  The turbine is site rated at approximately 33,526-shp at 60oF under base load conditions.  This project is necessary due to the increase in natural gas demand.  The project will significantly increase TWP’s ability to transport additional natural gas through an existing pipeline.  This project will also have significant environmental benefits resulting from a significant decrease in criteria pollutant emissions from the station.

TWP also proposes to replace the two existing generator engines with a single diesel generator package.  This unit will for backup power only.  TWP is proposing limited annual operating hours for this unit.  Manufacturer’s data was used to estimate NOx, CO, THC, and particulate emissions.  The latest version of AP-42 (10/96) for industrial diesel engines was used to estimate SO2 emissions. 

Existing equipment at the site is tabulated below:

Source Name
Emission Unit ID
Date of Installation

Ingersoll-Rand 616KVT 4000-hp Engine
P1
1966

Ingersoll-Rand 616KVT 4000-hp Engine
P2
1966

Ingersoll-Rand 616KVT 4000-hp Engine
P3
1966

Waukesha LRZ3520GU 451-hp Generator Engine
P4
1966

Waukesha LRZ3520GU 451-hp Generator Engine
P5
1966

Sivalls Heater 1.0 MMBtu/hr
P6
1966

Non-Point Sources
F1
1966

TWP is proposing to permanently shutdown P1, P2, P3, P4, and P5.  No changes are proposed for the remaining sources.  In addition to the existing sources listed above, the station is also equipped with the following sources identified as insignificant activities:

Source No.
Description

1
11,750 gallon lube oil tank

2
8,800 gallon lube oil tank

3
3,150 gallon used oil tank

4
5,040 gallon ethylene glycol tank

5
3,150 gallon ethylene glycol tank

6
8,820 gallon oily water tank

7
16,080 gallon oily water tank

8
23,100 gallon condensate tank

9
1,260 gallon condensate tank

10
vents, valves, flanges

At this time TWP proposes no changes to this list of insignificant activities.

A block flow diagram is included in this application.  Fuel fired by the engines and the proposed turbine is restricted to pipeline quality natural gas with negligible sulfur content.

2.1 Project Emissions

Average and maximum emissions of criteria pollutants from the proposed turbine are presented on Table 1.  Emissions of NOx, CO, and THC were provide by the turbine manufacturer.  Emissions vary over the ambient temperature and load range.  However, at base loads NOx and CO emissions are shown not to exceed 25 ppmv @ 15% O2.  Maximum mass NOx, CO, and THC emissions occur at 0oF at 64% load conditions.  This application represents maximum hourly emissions at this temperature and load condition.

Proposed annual emissions from the turbine were estimated on the assumption that the unit would operate at base load 80% of the time, and at reduced (64%) load the remaining 20% of the time.  This results in annual (tpy) emission limitations of 128.34, 78.27, and 2.65 for NOx, CO, and VOC respectively.  Hourly and annual VOC emissions are conservatively estimated assuming THC is 10% nm-VOC.  TWP has included a 15% safety factor in the proposed emissions for all pollutants.  Due to the extreme ambient temperature fluctuations in this area and its impact on turbine emissions, TWP believes this safety margin is justified.

Emissions of particulate, SO2, and formaldehyde (HAP) were estimated using the current version of AP-42 Section 3.1 (04/00) for gas turbines.  These emission factors are presented as lb/MMBtu.  Short term emissions of these pollutants were based on the worst case heat rate which occurs at 12.8oF.  Annual emissions were estimated using the worst case heat rate under base load conditions.  These emissions are insignificant and were not considered in the netting calculations.

Proposed emissions from the generator engine are shown on Table 2.  Emissions of NOx, CO, THC, and particulate were estimated using manufacturer’s data.  Emissions of SO2 emissions were estimated using the 10/96 version of AP-42 Section 3.3.

TWP anticipates operating the turbine 24 hours/day, 7 days/week, 52 weeks/year.  The generator engine is for backup purposes only and TWP is requesting a annual operating limitation of 2,000 hours.  It is anticipated that turbine and generator engine operations will be spread evenly (25%) over the spring, summer, fall, and winter quarters.  TWP is requesting no operating hour restrictions for the turbine and a 2,000 hour/year limitation on the diesel generator engine.

2.2 Netting Calculations

With regards to PSD applicability (40 CFR 52.21) the Kingman Compressor Station is classified as an existing major source of NOx and CO.  The original compressor and generator engines were installed in 1966 and have never been modified.  Therefore PSD applicability has never been triggered.  The proposed Red Rock Expansion Project will result in an increase in NOx and CO.  Evaluating the project on its own merits, the proposed NOx and CO emissions exceed the significance level defined by 40 CFR 52.21.  Therefore, PSD is potentially applicable to this project.

PSD applicability may be shown to be negative if it can be proven that the net emission increase does not exceed the significance levels.  This is accomplished by comparing the contemporaneous decreases and increases at the site.  If the net increase is less than the defined significance levels, then PSD would not be applicable.

A review of station records indicates that there have been no contemporaneous increases at the Kingman Compressor Station in the past five years.  Therefore, the only increases included in the netting calculations are from the proposed turbine and generator engine.  There have been no contemporaneous decreases at the station in the past five years.  Therefore the only decreases at the station to be considered in the netting calculations are from the permanent shutdown of the three existing Ingersoll-Rand reciprocating compressor engines and the two Waukesha LRZ3520GU generator engines.

Netting calculations are shown on Table 3.  Based on the netting calculations emissions of NOx and CO will be reduced significantly such that PSD review will not be applicable to this project.  The net change in particulate, VOC, and SO2 emissions are insignificant.

2.3 Alternative Operating Scenario Emissions

Due to the increase in demand for reliable natural gas delivery capabilities TWP is requesting an alternative operating scenario for this project.  As with any new project involving sophisticated equipment TWP needs to anticipate startup problems with the turbine and generator engines.  It is anticipated that this shake down period could take up to six (6) months to remedy.  Therefore, TWP is requesting that the ADEQ allow the use of the three reciprocating compressor engines as backups to the new equipment.  No alternative operating scenario is requested for the Waukesha generator engines.  These units will be permanently shutdown once the diesel unit is installed and operational.

Proposed alternative operating scenario emissions are shown on Table 4.  TWP proposes that the compressor engines be allowed a six month operating window beginning on the date of initial startup of the turbine.  At the end of this six month period the three Ingersoll-Rand compressor engines will be permanently shutdown and abandoned in-place.  TWP will not operate the Ingersoll-Rand compressor engines concurrently with the turbine.

The proposed six month operating window is based on calendar months, not on cumulative operating hours.  As required by 40 CFR 60 Subpart A, TWP will provide the ADEQ written notification of the turbine startup date.  Existing equipment will be permanently shutdown six months from this date.  Proposed emissions under the alternative scenario are based on potential engine emissions for six months (4,380 hours) of continuous operating time.  Since the engines will not be operated concurrently with the new equipment, PSD applicability will not be triggered under the alternative scenario since the past 2-year operating schedule exceeds the alternative operating scenario schedule.

When maintenance activities are required on gas turbines it is customary for the operator to replace the core power unit with a like kind unit, rather than replace the entire turbine package.  This type of replacement is considered routine maintenance for turbines.  TWP proposes that the permit contain a provision that allows written notification to the agency for this type of activity.  This flexibility will allow TWP to respond quickly to mechanical problems while minimizing gas delivery service interruptions.

2.4 Ambient Air Modeling

This project will result in a significant decrease in NOx and CO emissions from the Kingman Compressor Station.  Therefore, TWP proposes that ambient air modeling not be required since the project will result in an overall improvement in air quality.

2.5 BACT Analysis

TWP reviewed the EPA and California Air Resources Board BACT sites for recent control technology determinations.  BACT determinations are based on economic and technological feasibility.  The San Joaquin Valley Unified APCD has a listed BACT determination for a Southern California Gas Company gas compressor turbine having an enforceable NOx permit limitation of 25 ppmv @15% O2.   The proposed GE LM2500 has a NOx emission rate of 25 ppmv @15% O2 level at base load conditions.  Therefore, TWP proposes that the GE LM2500 gas turbine meets current BACT standards for this type of equipment.

The diesel generator engine is necessary for backup power only.  TWP is requesting enforceable limitations on operating hours.  Therefore, further reductions in emissions would be economically unreasonable.  TWP also proposes that the new diesel generator engine satisfies BACT standards for this type of equipment.  

3.0 AIR QUALITY REQUIREMENTS FOR SOURCES LOCATED IN ATTAINMENT AREAS (R18-2-304)

Arizona State Regulation R18-20-401(9)(b) specifies that specified source categories are considered major sources if emissions equal or exceed 100 tpy.  Non-category sources are considered to be major if emissions equal or exceed 250 tpy.  Equipment at the Kingman Compressor Station is not a listed source category.  However, potential emissions do exceed 250 tpy.  Based on existing equipment, the Kingman Compressor Station is classified as a major source.  When the permit is issued and the reciprocating engines are permanently shutdown, potential emissions of any single regulated pollutant will not exceed 250 tpy.

3.1 National and State Ambient Air Quality Standards

The existing national and state air quality standards are presented below:

Pollutant
Averaging Period
EPA Standards
Arizona Standards



Primary
Secondary
Primary
Secondary

PM10
Annual
50 ug/m3
50 ug/m3
50 ug/m3
50 ug/m3


24-hour
150 ug/m3
150 ug/m3
150 ug/m3
150 ug/m3

SO2
Annual
80 ug/m3
-
80 ug/m3
-


24-hour
365 ug/m3
-
365 ug/m3
-


3-hour
-
1300 ug/m3
-
1300 ug/m3

CO
8-hour
10 ug/m3
-
10 ug/m3
-


1-hour
40 ug/m3
-
40 ug/m3
-

NO2
Annual
100 ug/m3
100 ug/m3
100 ug/m3
100 ug/m3

Ozone
1-hour
235 ug/m3
235 ug/m3
235 ug/m3
235 ug/m3

The EPA and Arizona ambient air quality standards are the same.  Review of local air quality in the region around Kingman revealed that the local ambient air quality is better than state or federal standards.  The area is designated as a Class II attainment area for all criteria pollutants.

3.2 Regulatory Summary 

Federal regulations stipulate that a permit to construct a new major source or to modify an existing major source must undergo new source review to verify that the source will not cause or contribute to a violation of the NAAQS (see table above).  The proposed turbine is subject to NSR review by the Arizona DEQ.

3.2.1 Federal Regulatory Requirements

The Kingman Compressor Station is located in an area designated as attainment for all criteria pollutants.  Therefore, non-attainment regulations are not applicable to this facility.  The proposed project will result in a significant decrease in NOx and CO emissions.  These decreases offset the proposed increases such that netting shows that the PSD significance levels will not be exceeded.  Therefore, federal permitting (PSD or NNSR) is not required by this project.

New Source Performance Standards  (40 CFR 60)

The proposed turbine is subject to the requirements of 40 CFR Subpart GG – Standards of Performance for Stationary Gas Turbines (40 CFR 60.330).  TWP will comply with all applicable emission limits, testing, recordkeeping, and reporting requirements stipulated in the subpart and the general provisions (Subpart A).  

As allowed by the subpart, TWP is requesting the approval of a custom fuel monitoring schedule for the gas turbine.  The subpart requires operators to monitor fuel gas nitrogen and sulfur content on a daily basis.  However, the EPA routinely approves custom schedules for turbines that are fueled exclusively by sweet pipeline quality natural gas.  A proposed custom fuel monitoring schedule is included in Appendix B.

There are no NSPS standards for reciprocating engines.

National Emission Standards for Hazardous Air Pollutants (40 CFR 61)

There are no NESHAP standards which effect any existing or proposed sources located at the Kingman Compressor Station.

NESHAP for Source Categories (40 CFR 63) 

The only potentially applicable MACT requirements are Subparts HH and HHH.  These rules affect gas plants, and oil and gas storage and transmissions facilities which are classified as major sources of HAPs.  Emissions of any single HAP do not exceed 10 tpy and aggregate emissions of HAP do not exceed 25 tpy.  Therefore, the Kingman Compressor Station is not subject to either of these standards.

3.2.2 State Regulatory Requirements

TWP will comply with all applicable state regulatory requirements at the Kingman Compressor Station.  The existing Title V permit already stipulates the applicable regulatory requirements for which compliance is required.  These requirements were codified in the permit based on the representations in the Title V permit application.  TWP is operating the facility in compliance with these regulations.

The proposed turbine and generator engine installation project may require compliance with additional state regulations.  The following review addresses these potentially applicable requirements:

Title 18 Chapter 2 Article 6 – Emissions from Existing and New Nonpoint Sources

TWP will continue to comply with all of the applicable requirements of this article.  The Red Rock Expansion project will not result in the installation of any new nonpoint sources.

Title 18 Chapter 2 Article 7 – Existing Stationary Source Performance Standards

Existing equipment at the Kingman Compressor Station is not subject to any performance standards codified in this article.

Title 18 Chapter 2 Article 8 – Emissions from Mobile Sources (New and Existing)

Operations and equipment at the Kingman Compressor Station are not subject to the requirements of this article.  TWP will insure that company vehicles comply with all applicable standards for motor vehicles in Arizona.

Title 18 Chapter 2 Article 9 – New Source Performance Standards

The GE LM2500 turbine will comply with the applicable requirements of 40 CFR 60.330, Subpart GG.  The generator engine is not subject to any new source performance standard.

Title 18 Chapter 2 Article 11 – Federal Hazardous Air Pollutants

There are no applicable NESHAP or MACT standards at the Kingman Compressor Station.

Appendix A

Tables

Appendix B

Proposed Custom Fuel Monitoring Schedule

PROPOSED CUSTOM FUEL MONITORING SCHEDULE
FOR THE KINGMAN COMPRESSOR STATION

Stationary gas turbines subject to 40 CFR 60 Subpart GG shall only fire natural gas and may be allowed to utilize a custom fuel monitoring schedule, as an alternative provided for under 40 CFR, (60.334(b)(2), as long as the provisions are at least as stringent as the following.

(A)  Monitoring of fuel nitrogen is not required while pipeline quality natural gas is the only fuel fired in the gas turbine.

(B)  The fuel supplier or suppliers shall be identified for the record during turbine startup, and at any time that the fuel supplier or suppliers change.

(C)  Analysis for fuel sulfur content of the natural gas shall be conducted using one of the approved ASTM Test Methods for the measurement of sulfur in gaseous fuels, as referenced in 40 CFR, (60.335(d), or the Gas Processors Association (GPA) test method entitled “A Test for Hydrogen Sulfide and Carbon Dioxide in Natural Gas Using Length of Stain Tubes.”  The test methods are listed as follows:

(i)  ASTM D1072-80;

(ii)  ASTM D3031-81;

(iii)  ASTM D3246-81;

(iv)  ASTM D4084-82; or

(v)  GPA Standard 2377-86.

(D)  The owner or operator of a gas turbine who is not currently utilizing an approved custom fuel monitoring schedule shall be required to initially sample the fuel supply daily for a period of two weeks to establish, after turbine startup, that the pipeline quality natural gas fuel supply is low in sulfur content.

(E)  After the monitoring required in subparagraph (D) of this paragraph, sulfur monitoring shall be conducted twice monthly for six months.  If this monitoring shows little variability in the fuel sulfur content, and indicates consistent compliance with 40 CFR, (60.333(b), then sulfur monitoring shall be conducted once per quarter for six quarters.

(F)  If after the monitoring required in subparagraph (E) of this paragraph, or herein, the sulfur content of the fuel shows little variability and, calculated as sulfur dioxide, represents consistent compliance with the sulfur dioxide emission limits specified under 40 CFR, (60.333, sample analysis shall be conducted twice per annum.  This monitoring shall be conducted during the first and third quarters of each calendar year.

 (G)  Should any sulfur analysis as required in subparagraphs (E) or (F) of this paragraph indicate noncompliance with 40 CFR, (60.333, the owner or operator shall notify the commission within two weeks of such excess emissions.  The commission will then reexamine the custom schedule.  Sulfur monitoring shall be conducted weekly during the interim period when this custom schedule is being re-examined.

(H)  If there is a change in fuel supply (supplier), the owner or operator shall be required to sample the fuel daily for a period of two weeks to re-establish for the record that the fuel supply is low in sulfur content.  If the fuel suppliers low sulfur content is re-established, then the custom fuel monitoring schedule can be resumed.

(I)  Stationary gas turbines that use the same supply of pipeline quality natural gas to fuel multiple gas turbines may monitor the fuel sulfur content at a single common location.

Appendix C

General Electric LM2500 Data

Appendix D

Area Map, Process Flow Diagram, and Plot Plan
Appendix E

AP-42 Data Tables for Turbines and Engines

Appendix F

Generator Engine Data

Transwestern Pipeline Company

Kingman Compressor Station

Permit Application

Page 2 of 20

