12” Port Lavaca Loop Line

5/00 Leak

The following photos are of the holes found on the 12” pipe at the Port Lavaca Loop.  All of the holes were on the bottom of the pipe within a 20’ span.  Each hole was measured with a micrometer to determine their size.  There were additional holes not measured, that the corrosion technicians may have caused during their investigation. 

HOLE #1

[image: image1.jpg]



MEASSURED SIZE ID 0.115”

HOLE #2

[image: image2.jpg]



MEASURED SIZE ID 0.122”

HOLE #3,4 &5

[image: image3.jpg]



MEASURED SIZE ID

HOLE #3 – 0.077”

HOLE #4 – 0.027”

HOLE #5 – 0.027”

HOLE #6,7,8, & 9

[image: image4.jpg]



MEASURED SIZE

HOLE #6 – LENGTH - 0.4085”

                    WIDTH – 0.344”

                                   0.13”

                                   0.27”

               MEAN AVG. – 0.23825”

HOLE #7 – LENGTH – 0.1165”

                    WIDTH – 0.068”

HOLE #8 – LENGTH – 0.075”

                      WIDTH – 0.067”

HOLE #9 – LENGTH – 0.057”

                      WIDTH – 0.048”

HOLE #10

[image: image5.jpg]



MEASURED SIZE

LENGTH – 0.148”

WIDTH – 0.09”

HOLE #11

[image: image6.jpg]



MEASURED SIZE

LENGTH – 0.144”

   WIDTH – 0.072”

HOLE #12

[image: image7.jpg]



MEASURED SIZE

LENGTH – 0.071”

   WIDTH – 0.051”

HOLE #13

[image: image8.jpg]



MEASURED SIZE

LENGTH – 0.092”

WIDTH – 0.086”

HOLE #14, & 15

[image: image9.jpg]



MEASURED ID   

HOLE #14 – 0.03”

HOLE #15 – 0.03”

HOLE #16

[image: image10.jpg]



MEASURED ID – 0.0695”

HOLE #17

[image: image11.jpg]



MEASURED ID – 0.088”

[image: image12.jpg]



PICTURE SHOW WATER COMING OUT OF ONE OF THE HOLES DURING OUR INSPECTION.

[image: image13.jpg]
THE HOLES WHERE FOUND BETWEEN THE 20’ SECTION IN THE PICTURE ABOVE.

