Subject:
Lincoln Energy Center Due Diligence Questions

To:
Ben Rogers, Don Miller 

Don, 

Below is the response to the questions you posed for Lincoln Energy Center

1.   Relating to the plant's PSD permit:

     The Mostardi & Platt emissions test protocol for the May 2000

     Emissions test
The protocol for compliance stack testing at Lincoln Energy Center consists of:

1) Mostardi Platt emissions test protocol,

2) Leter from Dave Kellermeyer to IEPA requesting modification to the protocol and

3) Response e-mail from Shibu Vazha, IEPA approving the test protocol modifications

We will make those documents available to you. For your information the actual compliance stack test was initiated June 12, 2000

     A report to Illinois EPA containing the emission test data,

     Continuous Emission Monitoring ("CEM") Data (all data

     developed since start-up)
Mostardi Platt prepared a compliance stack testing report    detailing the results from the testing initiated June 12th. We will make this document available to you.

CEMs Certification Testing was recently completed in August, 2000. Because the CEMs system was not certified, the requirement to submit has only recently been encountered. 3rd Quarterly CEMS Emission Data Reports (EDR) submittals to IEPA have not, as yet been submitted to IEPA. 

Any reports to IEPA required under the permit pertaining to

exceedances, or start-up, breakdown & malfunction (internal memos indicate that there was a breakdown at # 7 on July 5, 2000)
We are aware of no plant conditions encountered that per permit conditions require reporting to the IEPA. The CEMS was certified on July 31, 2000 within 90 days from commencement of commercial operation. We are not required to report CEMS breakdown prior to CEMS certification.

2. Also, we don't have any permits for wastewater discharge. We have been told that there is no wastewater discharged except

sewage/office wastewater which is going to a septic field. But we have no verification of this at this point.

The plant has chosen not to discharge wastewater generated on site. Instead, wastewater is temporarily stored in a tank and the hauled to a permitted wastewater treatment facility. 

