ENRON






   Interoffice
CORP






   Memorandum

To:

Ted Bland
From:

Robert D. Morgan

Subject:
Hydraulics for 8” Nacogdoches Lateral


Date:  February 23, 1999

___________________________________________________________________________________

At this time, the capacity of the 8” Nacogdoches lateral to Tufco is about 17MM/D.  It is based on VERY general information.  As I receive more information, I can offer more specific recommendations and options.

Since a lot of detailed information is still forthcoming,  I made several educated guesses, shown below.

1) the MAOP is at least 800psig,

2)  the pipeline efficiency is 90%,

3) the 50’ of 4” pipe will be replaced,

4) the 1500-2000’ of 6” pipe will be replaced or looped,

5) the Texoma pressures will vary between 700-750psig,

6) Tufco’s pressures are 550-650psig.

A table of the results are shown below.


Pressures

Texoma
Tufco

Volume
Comments







650psig
550psig
17MM/D
Existing capacity



700psig
550psig
22MM/D
Possible with operating changes



700psig
650psig
14MM/D



750psig
550psig
26MM/D



750psif

650psig
18MM/D



800psig
550psig
31MM/D



800psig
650psig
25MM/D



1000psig
550psig
46MM/D
Add 750hp unit on 8”

When I spoke to Lyndon Reynolds, I requested a schematic of their Storage, Stryker Plant, and associated piping.  He is working on that and an explanation of what dictates their pipeline pressures.  I hope to have it next week.

NAC9-01

