2000 Summer Path 26 OTC Upgrading (3000MW) Study


2000 Summer

Path 26 (Midway-Vincent)

Operating Transfer Capability Increase Study Report

Submitted to

California Operations Studies Subcommittee

&

Operating Transfer Capability Policy Group

By

California Independent System Operator

Mark Willis

Chuck-yan Wu

 August 16, 2000

Executive Summary

The purpose of this study is to support the increase of the Operating Transfer Capability (OTC) of Path 26 to its full rating of 3000 MW from the currently approved OTC of 2800 MW for the remaining 2000 Summer operating season.

Path 26 (Midway – Vincent 500 kV lines #1, #2, and #3) was thermally limited by the emergency rating (3000 Amps, or 2800 MW) of the wavetraps in the Midway – Vincent #3 500 kV line at the Midway and Vincent for the loss of  #1 & #2 lines.  PG&E and SCE had recently submitted to CAISO an updated emergency rating for the wavetraps, thus enabling Path 26 be loaded to its pre-contingency full WSCC path rating of 3000 MW.

The impact of Path 26 flow at 3000 MW to the existing nomogram operations (COI/DC, and SCIT) were studied using the 2000 summer nomogram point cases. Study results, showed in Tables 1 and 2, indicated that the increase flow on Path 26 have NO significant impact on the simultaneous limits of the current OTCs and nomogram operations of COI/DC and SCIT:

· Post-contingency flows are all within emergency limits.

· All major buses that are monitored maintained their post-contingency var margins.

· The system is stable.

· Study Methodology is attached

Path
Summer 2000 OTC

COI (N-S)
4,600MW*

PDCI (N-S)
3,100MW*

Path 26
3,000MW

SCIT
13,000MW*

Maximum SDG&E Import
2,750MW*
3,050MW*

Maximum CFE Import
400MW*


* No change in OTC.

[image: image1.wmf]California EHV Transmission System

Encina

SONGS

Note: Also part

of Path 46

Control

Craig View

Weed

Junction

PIT River

  (Hydro)

Mission

Imperial Valley

Adelanto

Miguel

Palo

Verde

Devers

Valley

Serrano

Mira 

Loma

Lugo

Victorville

Rinaldi

Mohave

Eldorado

Mc 

Cullough

Market Place

Toluca

Midway

Diablo Canyon

Gates

Los

Banos

Sylmar

Intermountain

Celilo

Malin

Captain Jack

Southbay

Tesla

Metcalf

Moss

Landing

Tracy

Vaca

Dixon

Table

Mountain

Round

Mountain

Olinda

McCall

Panoche

Morro Bay

Helms

Santiago

Chino

CFE

CFE

Talega

Escondido

Mead

El Centro

Mirage

Coachella

West of River

Vincent

Feather River

     (Hydro)

Shasta

Keswick

Geysers

Hunters Point

Protrero

Pittsburg

San Luis

Big Creek

   (Hydro)

Kings River

Castaic

Cascade

Meridian

Drum

Summit

Inyo

Silver Peak

Transfer Paths/Rating

2000 Summer OTC

Path 15

North /South:

  Limited by Path 26 flow

South / North

 3450MW

Path 26

3000MW  N/S

 2800MW

Path 27

1920MW E/W

 Limited by SCIT Total

Path 44

1800MW N-S

 Limited by Total Import to

 SDG&E and CFE

Path 45

408 MW Bi-directional

Path 46

10,118 MW E/W

Limited by SCIT Total

Path 49

7550MW E/W

Limited by SCIT Total

Path 65

3100 N/S

3100MW

(PDCI)

Path 66

4800MW N/S

 4600MW

(COI)

SCIT

18860 MW

13,000MW

Hoover

Colorado River

Contra

Costa

MEXICO

USA

Colorado River

(Path 65)

(

Path 66)

Stability

(Path 25)

(Path 24)

  Stability

Thermal

Note: Also part

of Path 46

East of River

USF Path 21

(Path 27)

Gregg

Bellota

Hyatt (CDWR)

Aqueduct

Mandaly

Ormond Beach

Pardee

Huntington

Beach

Newark

Navajo

Moenkopi

Liberty

Perkins

North

Gila

Maxwell

(WAPA)

(Path 15)

(Path 60)

(Path 49)

(Path 46)

(Path 61)

(Path 26)

(Path 42)

(Path 41)

(Path 43)

(Path 44)

(Path 45)

 Limited by Total Import to

 SDG&E and CFE


[image: image2.wmf]Inertia

Malin

Victo

r 

Devers

Miral

oma

Migue

l

South 

Bay

Miguel

TJI 

South 

Bay

Case Description

MWs

SCIT

COI

P-26

WOR

EOR

PDCI

IPP

SDGE/

CFE 

Import

SDGE-

CFE

Contingency

500

500

500

500

500

69

230

230

138

hs_s13_p29_m28_s2750_c300_swplcaps_2els

13025

4597

2803

5612

4948

2965

1763

3053

307

 

Load + losses:

12819

5434

3822

6083

5215

2965

0

2988

273

IPP BIPOLE

985

3000

1316

2637

525

230

578

420

488

PG&E:  20865 MW

12815

5453

3840

6062

5185

2965

0

2988

273

IPP - CRSTMC

969

3000

1313

2634

517

230

569

413

485

SCE:  18047 MW

13101

4684

2899

5589

4890

2965

1763

3103

304

IV-MG RAS - TJI

1752

2558

1155

1590

203

159

258

164

267

SDG&E:  3581 MW

13101

4711

2930

5557

4813

2965

1763

3103

304

IV - NGILA

1692

2486

1067

1629

249

205

272

232

336

LADWP:  5475 MW

13023

4631

2837

5571

4938

2965

1763

3048

307

LUGO-ELD/MOH

1792

3000

1285

2563

512

227

558

407

476

CFE:  1667 MW

13074

4551

2767

5696

5001

2965

1763

3051

306

DOUBLE M/V

1919

2979

1274

2379

512

228

564

411

479

12723

6020

4474

6272

5319

0

1763

2948

253

PDCI BIPOLE

1615

2571

1228

2210

210

227

554

399

475

13062

4668

2877

5570

4821

2965

1763

3050

308

PV-DEVERS

1762

2786

614

2010

447

214

474

326

414

13094

4731

2952

5528

4649

2965

1763

3102

305

PV-N.GILA

1694

2491

969

1473

166

169

182

154

229

14998

5710

4154

6220

5322

2965

1763

2968

265

2 SONGS

592

601

396

350

80

80

76

67

88

Stress Path 26 to 3000MW

00hs_p3000

13016

4583

3006

5400

4787

2965

1763

3046

307

Pre-Contingency

12810

5416

4026

5871

5055

2965

0

2977

273

IPP BIPOLE

996

3000

1335

2628

541

232

12806

5433

4042

5851

5027

2965

0

2977

273

IPP - CRSTMC

962

3000

1330

2629

534

232

13091

4667

3099

5380

4732

2965

1763

3095

304

IV-MG RAS - TJI

1763

2596

1184

1619

204

160

IV - NGILA

LUGO-ELD/MOH

Limiting Remaining Line #3 -- 3000MW -->

13073

4534

2970

5493

4846

2965

1763

3043

306

DOUBLE M/V

1918

2950

1278

2290

525

229

12720

6002

4681

6063

5161

0

1763

2941

254

PDCI BIPOLE

1616

2567

1237

2191

517

229

13051

4649

3076

5362

4667

2965

1763

3042

308

PV-DEVERS

1775

2832

614

2012

463

220

13085

4713

3151

5321

4488

2965

1763

3095

305

PV-N.GILA

1714

2425

992

2728

170

172

14994

5692

4361

6011

5163

2965

1763

2960

265

2 SONGS

593

705

442

392

93

92

Notes:

1)  Adelanto SVC inserted

2)  System Swing bus is Encina 5

3)  SCE capacitors modeled as SVDs and allowed to float

4)  SDG&E capacitors modeled as SVDs and allowed to float

5)  IID 230/161 kV Transformer using 115% Emergency Rating per IID

6)  Bypassed 1 SWPL capacitor to alleviate steady-state SWPL overload (In IV-NG @ NG)

7)  Moved PST's at Perkins to 600 MW each bank to alleviate SWPL overload

Var Margin (Mvar) Monitoring

Table 1. Path 26 (3000MW) Sensitivity -- 2000 Summer EOR/SCIT Paths OTC Study Results

Flows



Table 2.  Impact to AC/DC Nomogram Operation

Attachment:  Study Methodology

1. Background

The purpose of this study is to verify the operating transfer capability of COI, PDCI, Path 26, SCIT and SDG&E/CFE total import limitations for the 2000 Summer operating season.

[image: image3.wmf]POST-TRANSIENT

 

MVAR MARGIN

% N. 

Cal. 

Hydro

Description

AC+  

DC

AC+

NCH

COI

PDCI 

(P.O.)

M/V

MP-SL    

FLOW

NE/SE 

FLOW

NJD  

RATS

SCIT

2 PV             

(BPA)

2 PV 

(PG&E)

2   

DC  

PP

2 ML  

PP

2 P  

PP

DC                

(BPA)

DC 

(PG&E)

MAS 

DLO

RMS 

DLO

TMS   

DLO

TSN  

DLO

TSTR-

TRLB

MV 

DLO

OLTR 

SLO

55%

hs_c46_p29_h55_m28_ms4_s12  

(Nomogram Point)

7578

6841

4613

2965

2791

426

1160

7699

-2

12152

212 - GR

281 - RM

697 - 

OS

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

55%

5% COI Test

7667

6930

4702

2965

2778

424

1174

7784

-2

12151

7- GR

21 - RM

-

-

-

-

-

-

-

-

-

-

-

-

55%

2.5% COI Test

0

2228

0

 

 

 

 

 

 

 

 

 

-

-

-

-

-

-

-

-

-

-

-

-

55%

100 MW Stability Test

0

####

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

60%

hs_c46_p29_h60_m28_ms4_s12

7567

7032

4602

2965

2781

418

1171

7695

-1

12152

174 - GR

255 - RM

642 - 

DX

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

60%

hs_c455_p29_h60_m28_ms4_s12 

(Nomogram Point)

7521

6986

4556

2965

2809

420

1166

7701

-1

12174

234 - OS

319 - RM

 

70%

hs_c45_p29_h70_m28_ms4_s12

7471

7341

4506

2965

2811

403

1193

7716

-1

12200

204 - GR

267 - RM

680 - 

DX

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

70%

hs_c445_p29_h70_m28_ms4_s12 

(Nomogram Point)

7418

7288

4453

2965

2801

407

1184

7714

-1

12182

276 - OS

379 - RM

 

 

80%

hs_c44_p29_h80_m28_ms4_s12

7363

7638

4398

2965

2805

384

1211

7704

5

12210

140 - GR

199 - RM

651 - 

DX

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

80%

hs_c43_p29_h80_m28_ms4_s12 

(Nomogram Point)

7269

7544

4304

2965

2805

389

1196

7700

5

12197

275 - CJ

376 - RM

80%

hs_c43_p29_h80_m30_ms4_s12 

(Nomogram Point)

7258

7533

4293

2965

2994

378

1207

7697

4

12395

281 - GR

413 - RM

-

-

-

> 1000

> 1000

-

-

-

-

-

-

-

80%

hs_c43_p29_h80_m28_ms0_s12  (MP-

SL Test)

7273

7548

4308

2965

2859

46

1012

7581

5

11892

138 - OS

211 - RM

-

-

-

-

-

-

-

-

-

-

-

-

80%

hs_c42_p29_h80_m28_ms0_s13  (MP-

SL Test)

7173

7448

4208

2965

2863

47

1006

7605

5

11892

252 - CJ

358 - RM

-

-

-

-

-

-

-

-

-

-

-

-

 

90%

hs_c43_p29_h90_m28_ms4_s12

7270

7950

4305

2965

2811

374

1226

7712

2

12230

151 - GR

200 - RM

665 - 

DX

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

90%

hs_c42_p29_h90_m28_ms4_s12 

(Nomogram Point)

7173

7853

4208

2965

2802

380

1210

7701

2

12207

281 - GR

401 - RM

 

 

 

100%

hs_c42_p29_h100_m28_ms4_s12

7162

8247

4197

2965

2804

366

1224

7706

9

12220

83 - HF

44 - RM

628 - 

GR

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

100%

hs_c40_p29_h100_m28_ms4_s12 

(Nomogram Point)

6973

8058

4008

2965

2812

370

1206

7700

9

12213

208 - GR

305 - RM

 

* Lower Columbia generation includes: The Dalles, John Day, Bonneville, and McNary.

** 230 kV Capacitors at Vaca-Dixon, Tesla, and Metcalf were switched in as well as 132 MVAr SVC at Adelanto 500 kV in the post-transient routine.

California EHV Transmission System

2. Methodology

The WSCC reliability criteria, the WSCC voltage stability criteria, and member reliability criteria as appropriate were used to evaluate the adequacy of study results. 

· General Methodology

1. The basecases used in this study were developed from the OTC 00hs03b case. 

2.
Governor action will be assumed throughout the WSCC system for generator outage(s).


· Steady-state
· No system element is loaded more than 100% of its continuous thermal rating under pre-contingency conditions.

· No system element is loaded more than 100% of the emergency thermal rating after a contingency.

· Transient Stability


· Transient stability runs will be run out to 20 seconds to ensure the system is stable and positively damped. 


· Steam governors will be blocked as per the TSS recommendation


· The load type will be submitted by the utilities during the base case development process.  The default  load type for the NW and BC-Hydro areas will be set at 100% constant current for P and 100% constant impedance for Q.


· Acceleration Trend Relay (ATR): Suspected ATR action will be verified by Montana Power Company if there is an indication of separation between Montana and the Northwest neighboring areas, or there are sustained low voltages in the Montana area or on its interties.  Information required will be the accelerating power, machine angle, speed and MW loading for each Colstrip machine.  The GE program has a model for the ATR that has not been verified by Montana.  However, it may give an indication when a Colstrip unit trip is needed.


· Additional RAS used in transient stability analysis:

· Insert 21 ohms Fort Rock series capacitors (fast insertion) between Grizzly and Captain Jack, Grizzly and Malin, Buckley and Summer Lake.

· Refer to an updated table Northwest Generator Drop for Bipolar PDCI Outage (n-s) for amount and timing of generator dropping in Northwest.

· Drop filter banks at Celilo and Sylmar (the MVAR levels dropped will depend upon the DC schedule).

· Insert 400 MVAR of MSC @ Malin, 200 MVAR shunt capacitor @ Olinda, 600 MVAR shunt capacitor @ Tracy, 454 MVAR shunt capacitor @ Table Mt.

· The WSCC Reliability Criteria for Transmission System Planning will be observed for the transient stability results. 

· Post transient

· Margin: In compliance with the new TSS Margin Criteria, the operating transfer capability study will meet the N-1 reactive margin criteria, and the N-2 criteria will be assumed (50% of N-1).  In particular, North of Malin, the Northwest 500 kV bus reactive margin requirement is 600 MVAR for N-1, and 300 MVAR for N-2.  In California, (except SDG&E) all 500 kV bus reactive margin requirement is 500 MVAR for N-1 and 250 MVAR for N-2.  SDG&E’s reactive margin requirement is 150 MVAr for N-1 and 75 MVAr for N-2 for all buses 230 kV above and at generating plant buses. 

· Power margin test will be performed on all paths being studied.  This would include stressing the path 5% for N-1 and 2.5% for N-2.  The system needs to have positive reactive margin.


· Double generator outages are required to meet WSCC Performance Level C.


· A maximum voltage dip of 5% in Idaho, Utah, and Southern Oregon system.


· Additional RAS used in post-transient:

(a) remove all Sylmar filter banks.

(b) insert 175 MVAR shunt capacitor @ Kinport if the voltage drops to 0.96 p.u. and sustains for 3 seconds.

(c) Insert 126 MVAR shut capacitors @ Vaca-Dixon 230, 252 MVAR @ Tesla 230, and 375 MVAR @ Metcalf 230 based on local voltage control
(d) Insert 132 MVAR SVC at Adelanto if Adelanto voltage dip beyond 5%.

(e) IV-Miguel line outage RAS updated to cross trip Miguel-Tijuana 230 kV Line.

· Other

· The maximum permissible 2700 MW generator drop in the Northwest is an integral part of the RAS, which mitigates the impact of a PDCI bipolar outage.

· Northwest FACRI is available to all contingencies.

3. Study Results

· Contingency Screening

The worst contingencies in California including the following:

1) 2 PV unit Outage

2) Bipolar outage of the PDCI

3) Table Mountain South Double Line Outage  

4) 2 SONGS unit Outage

5) SWPL Line Outage/with RAS

6) 2 Diablo Canyon unit Outage

7) 2 Moss Landing Unit Outage

8) 2 Pittsburg Unit Outage

· AC/DC/Northern California Hydro Nomogram 

For Northern California the worst contingency is the loss of 2 PV units (G-2), the loss of PDCI Bipolar (N-1), the loss of 2 Moss Landing Units, and the Table Mountain South Double Line Outage (N-2).  The limiting factor is the reactive margin at Round Mountain and various Northwest 500 kV buses (Grizzly 500) for loss of 2PV units.

· SCIT Nomogram

For SCIT and Southern California, the worst contingencies are the loss of 2 SONGS units (N-2), loss of IV-Miguel (cross trip Miguel-Tijuana 230), and the loss of PV-N.Gila line. The limiting factor is the reactive margin at the South Bay 69 kV bus in SDG&E.

The study results are based on Midway-Vincent flow of 3000 MW and COI flow of 4600 MW. SDG&E/CFE total import of 3050MW.

A sensitivity study analyzing the potential relationship between the SCIT and the SDG&E/CFE Import was conducted.  The SDG&E/CFE Import was reduced to 2,145 MW from 3,050 MW, and the SCIT was raised until the reactive margin criteria was satisfied for the loss of two San Onofre Nuclear Generating Station units.  The inertia in Southern California (LADWP, SCE, and SDG&E) remained constant between the OTC study and the sensitivity.  The results illustrated that the SCIT could achieve a minimum of 15,500 MW.  However, the results are based on additional generating units in the Southern California Edison (SCE) area beyond both the required Reliability Must-Run (RMR) generating units and units required to meet load in Southern California Edison area.  These additional generating units would not necessarily be on-line unless provided by the market, and would not be required on-line for RMR.  Studies were also analyzed without the additional generating units in the SCE area with the 2,145 MW SDG&E/CFE Import, and the SCIT remained approximately unchanged.

� EMBED Word.Picture.8  ���





� EMBED Excel.Sheet.8  ���





� EMBED Excel.Sheet.8  ���











1

[image: image4.wmf]California EHV Transmission System

Encina

SONGS

Note: Also part

of Path 46

Control

Craig View

Weed

Junction

PIT River

  (Hydro)

Mission

Imperial Valley

Adelanto

Miguel

Palo

Verde

Devers

Valley

Serrano

Mira 

Loma

Lugo

Victorville

Rinaldi

Mohave

Eldorado

Mc 

Cullough

Market Place

Toluca

Midway

Diablo Canyon

Gates

Los

Banos

Sylmar

Intermountain

Celilo

Malin

Captain Jack

Southbay

Tesla

Metcalf

Moss

Landing

Tracy

Vaca

Dixon

Table

Mountain

Round

Mountain

Olinda

McCall

Panoche

Morro Bay

Helms

Santiago

Chino

CFE

CFE

Talega

Escondido

Mead

El Centro

Mirage

Coachella

West of River

Vincent

Feather River

     (Hydro)

Shasta

Keswick

Geysers

Hunters Point

Protrero

Pittsburg

San Luis

Big Creek

   (Hydro)

Kings River

Castaic

Cascade

Meridian

Drum

Summit

Inyo

Silver Peak

Transfer Paths/Rating

2000 Summer OTC

Path 15

North /South:

  Limited by Path 26 flow

South / North

 3450MW

Path 26

3000MW  N/S

 2800MW

Path 27

1920MW E/W

 Limited by SCIT Total

Path 44

1800MW N-S

 Limited by Total Import to

 SDG&E and CFE

Path 45

408 MW Bi-directional

Path 46

10,118 MW E/W

Limited by SCIT Total

Path 49

7550MW E/W

Limited by SCIT Total

Path 65

3100 N/S

3100MW

(PDCI)

Path 66

4800MW N/S

 4600MW

(COI)

SCIT

18860 MW

13,000MW

Hoover

Colorado River

Contra

Costa

MEXICO

USA

Colorado River

(Path 65)

(

Path 66)

Stability

(Path 25)

(Path 24)

  Stability

Thermal

Note: Also part

of Path 46

East of River

USF Path 21

(Path 27)

Gregg

Bellota

Hyatt (CDWR)

Aqueduct

Mandaly

Ormond Beach

Pardee

Huntington

Beach

Newark

Navajo

Moenkopi

Liberty

Perkins

North

Gila

Maxwell

(WAPA)

(Path 15)

(Path 60)

(Path 49)

(Path 46)

(Path 61)

(Path 26)

(Path 42)

(Path 41)

(Path 43)

(Path 44)

(Path 45)

 Limited by Total Import to

 SDG&E and CFE

[image: image5.wmf]POST-TRANSIENT

 

MVAR MARGIN

% N. 

Cal. 

Hydro

Description

AC+  

DC

AC+

NCH

COI

PDCI 

(P.O.)

M/V

MP-SL    

FLOW

NE/SE 

FLOW

NJD  

RATS

SCIT

2 PV             

(BPA)

2 PV 

(PG&E)

2   

DC  

PP

2 ML  

PP

2 P  

PP

DC                

(BPA)

DC 

(PG&E)

MAS 

DLO

RMS 

DLO

TMS   

DLO

TSN  

DLO

TSTR-

TRLB

MV 

DLO

OLTR 

SLO

55%

hs_c46_p29_h55_m28_ms4_s12  

(Nomogram Point)

7578

6841

4613

2965

2791

426

1160

7699

-2

12152

212 - GR

281 - RM

697 - 

OS

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

55%

5% COI Test

7667

6930

4702

2965

2778

424

1174

7784

-2

12151

7- GR

21 - RM

-

-

-

-

-

-

-

-

-

-

-

-

55%

2.5% COI Test

0

2228

0

 

 

 

 

 

 

 

 

 

-

-

-

-

-

-

-

-

-

-

-

-

55%

100 MW Stability Test

0

####

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

60%

hs_c46_p29_h60_m28_ms4_s12

7567

7032

4602

2965

2781

418

1171

7695

-1

12152

174 - GR

255 - RM

642 - 

DX

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

60%

hs_c455_p29_h60_m28_ms4_s12 

(Nomogram Point)

7521

6986

4556

2965

2809

420

1166

7701

-1

12174

234 - OS

319 - RM

 

70%

hs_c45_p29_h70_m28_ms4_s12

7471

7341

4506

2965

2811

403

1193

7716

-1

12200

204 - GR

267 - RM

680 - 

DX

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

70%

hs_c445_p29_h70_m28_ms4_s12 

(Nomogram Point)

7418

7288

4453

2965

2801

407

1184

7714

-1

12182

276 - OS

379 - RM

 

 

80%

hs_c44_p29_h80_m28_ms4_s12

7363

7638

4398

2965

2805

384

1211

7704

5

12210

140 - GR

199 - RM

651 - 

DX

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

80%

hs_c43_p29_h80_m28_ms4_s12 

(Nomogram Point)

7269

7544

4304

2965

2805

389

1196

7700

5

12197

275 - CJ

376 - RM

80%

hs_c43_p29_h80_m30_ms4_s12 

(Nomogram Point)

7258

7533

4293

2965

2994

378

1207

7697

4

12395

281 - GR

413 - RM

-

-

-

> 1000

> 1000

-

-

-

-

-

-

-

80%

hs_c43_p29_h80_m28_ms0_s12  (MP-

SL Test)

7273

7548

4308

2965

2859

46

1012

7581

5

11892

138 - OS

211 - RM

-

-

-

-

-

-

-

-

-

-

-

-

80%

hs_c42_p29_h80_m28_ms0_s13  (MP-

SL Test)

7173

7448

4208

2965

2863

47

1006

7605

5

11892

252 - CJ

358 - RM

-

-

-

-

-

-

-

-

-

-

-

-

 

90%

hs_c43_p29_h90_m28_ms4_s12

7270

7950

4305

2965

2811

374

1226

7712

2

12230

151 - GR

200 - RM

665 - 

DX

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

90%

hs_c42_p29_h90_m28_ms4_s12 

(Nomogram Point)

7173

7853

4208

2965

2802

380

1210

7701

2

12207

281 - GR

401 - RM

 

 

 

100%

hs_c42_p29_h100_m28_ms4_s12

7162

8247

4197

2965

2804

366

1224

7706

9

12220

83 - HF

44 - RM

628 - 

GR

> 

1000

> 

1000

> 1000

> 1000

> 1000

> 1000

> 

1000

> 

1000

> 1000

> 

1000

> 1000

100%

hs_c40_p29_h100_m28_ms4_s12 

(Nomogram Point)

6973

8058

4008

2965

2812

370

1206

7700

9

12213

208 - GR

305 - RM

 

* Lower Columbia generation includes: The Dalles, John Day, Bonneville, and McNary.

** 230 kV Capacitors at Vaca-Dixon, Tesla, and Metcalf were switched in as well as 132 MVAr SVC at Adelanto 500 kV in the post-transient routine.

[image: image6.wmf]Inertia

Malin

Victo

r 

Devers

Miral

oma

Migue

l

South 

Bay

Miguel

TJI 

South 

Bay

Case Description

MWs

SCIT

COI

P-26

WOR

EOR

PDCI

IPP

SDGE/

CFE 

Import

SDGE-

CFE

Contingency

500

500

500

500

500

69

230

230

138

hs_s13_p29_m28_s2750_c300_swplcaps_2els

13025

4597

2803

5612

4948

2965

1763

3053

307

 

Load + losses:

12819

5434

3822

6083

5215

2965

0

2988

273

IPP BIPOLE

985

3000

1316

2637

525

230

578

420

488

PG&E:  20865 MW

12815

5453

3840

6062

5185

2965

0

2988

273

IPP - CRSTMC

969

3000

1313

2634

517

230

569

413

485

SCE:  18047 MW

13101

4684

2899

5589

4890

2965

1763

3103

304

IV-MG RAS - TJI

1752

2558

1155

1590

203

159

258

164

267

SDG&E:  3581 MW

13101

4711

2930

5557

4813

2965

1763

3103

304

IV - NGILA

1692

2486

1067

1629

249

205

272

232

336

LADWP:  5475 MW

13023

4631

2837

5571

4938

2965

1763

3048

307

LUGO-ELD/MOH

1792

3000

1285

2563

512

227

558

407

476

CFE:  1667 MW

13074

4551

2767

5696

5001

2965

1763

3051

306

DOUBLE M/V

1919

2979

1274

2379

512

228

564

411

479

12723

6020

4474

6272

5319

0

1763

2948

253

PDCI BIPOLE

1615

2571

1228

2210

210

227

554

399

475

13062

4668

2877

5570

4821

2965

1763

3050

308

PV-DEVERS

1762

2786

614

2010

447

214

474

326

414

13094

4731

2952

5528

4649

2965

1763

3102

305

PV-N.GILA

1694

2491

969

1473

166

169

182

154

229

14998

5710

4154

6220

5322

2965

1763

2968

265

2 SONGS

592

601

396

350

80

80

76

67

88

Stress Path 26 to 3000MW

00hs_p3000

13016

4583

3006

5400

4787

2965

1763

3046

307

Pre-Contingency

12810

5416

4026

5871

5055

2965

0

2977

273

IPP BIPOLE

996

3000

1335

2628

541

232

12806

5433

4042

5851

5027

2965

0

2977

273

IPP - CRSTMC

962

3000

1330

2629

534

232

13091

4667

3099

5380

4732

2965

1763

3095

304

IV-MG RAS - TJI

1763

2596

1184

1619

204

160

IV - NGILA

LUGO-ELD/MOH

Limiting Remaining Line #3 -- 3000MW -->

13073

4534

2970

5493

4846

2965

1763

3043

306

DOUBLE M/V

1918

2950

1278

2290

525

229

12720

6002

4681

6063

5161

0

1763

2941

254

PDCI BIPOLE

1616

2567

1237

2191

517

229

13051

4649

3076

5362

4667

2965

1763

3042

308

PV-DEVERS

1775

2832

614

2012

463

220

13085

4713

3151

5321

4488

2965

1763

3095

305

PV-N.GILA

1714

2425

992

2728

170

172

14994

5692

4361

6011

5163

2965

1763

2960

265

2 SONGS

593

705

442

392

93

92

Notes:

1)  Adelanto SVC inserted

2)  System Swing bus is Encina 5

3)  SCE capacitors modeled as SVDs and allowed to float

4)  SDG&E capacitors modeled as SVDs and allowed to float

5)  IID 230/161 kV Transformer using 115% Emergency Rating per IID

6)  Bypassed 1 SWPL capacitor to alleviate steady-state SWPL overload (In IV-NG @ NG)

7)  Moved PST's at Perkins to 600 MW each bank to alleviate SWPL overload

Var Margin (Mvar) Monitoring

Table 1. Path 26 (3000MW) Sensitivity -- 2000 Summer EOR/SCIT Paths OTC Study Results

Flows



_1027926805.xls
Path26 Sensitivity

		Table 1. Path 26 (3000MW) Sensitivity -- 2000 Summer EOR/SCIT Paths OTC Study Results

																										Var Margin (Mvar) Monitoring																		Stability

				Inertia		Flows																				Malin		Victor ville		Devers		Miraloma		Miguel		South Bay		Miguel		TJI		South Bay		Comments

		Case Description		MWs		SCIT		COI		P-26		WOR		EOR		PDCI		IPP		SDGE/CFE Import		SDGE-CFE		Contingency		500		500		500		500		500		69		230		230		138

		hs_s13_p29_m28_s2750_c300_swplcaps_2els				13025		4597		2803		5612		4948		2965		1763		3053		307

		Load + losses:				12819		5434		3822		6083		5215		2965		0		2988		273		IPP BIPOLE		985		3000		1316		2637		525		230		578		420		488		Stable

		PG&E:  20865 MW				12815		5453		3840		6062		5185		2965		0		2988		273		IPP - CRSTMC		969		3000		1313		2634		517		230		569		413		485		Stable

		SCE:  18047 MW				13101		4684		2899		5589		4890		2965		1763		3103		304		IV-MG RAS - TJI		1752		2558		1155		1590		203		159		258		164		267		Stable

		SDG&E:  3581 MW				13101		4711		2930		5557		4813		2965		1763		3103		304		IV - NGILA		1692		2486		1067		1629		249		205		272		232		336		Stable

		LADWP:  5475 MW				13023		4631		2837		5571		4938		2965		1763		3048		307		LUGO-ELD/MOH		1792		3000		1285		2563		512		227		558		407		476		Stable

		CFE:  1667 MW				13074		4551		2767		5696		5001		2965		1763		3051		306		DOUBLE M/V		1919		2979		1274		2379		512		228		564		411		479		Stable

						12723		6020		4474		6272		5319		0		1763		2948		253		PDCI BIPOLE		1615		2571		1228		2210		210		227		554		399		475		Stable

						13062		4668		2877		5570		4821		2965		1763		3050		308		PV-DEVERS		1762		2786		614		2010		447		214		474		326		414		Stable

						13094		4731		2952		5528		4649		2965		1763		3102		305		PV-N.GILA		1694		2491		969		1473		166		169		182		154		229		Stable

						14998		5710		4154		6220		5322		2965		1763		2968		265		2 SONGS		592		601		396		350		80		80		76		67		88		Stable

		Stress Path 26 to 3000MW

		00hs_p3000				13016		4583		3006		5400		4787		2965		1763		3046		307		Pre-Contingency

						12810		5416		4026		5871		5055		2965		0		2977		273		IPP BIPOLE		996		3000		1335		2628		541		232

						12806		5433		4042		5851		5027		2965		0		2977		273		IPP - CRSTMC		962		3000		1330		2629		534		232

						13091		4667		3099		5380		4732		2965		1763		3095		304		IV-MG RAS - TJI		1763		2596		1184		1619		204		160

																								IV - NGILA

																								LUGO-ELD/MOH

		Limiting Remaining Line #3 -- 3000MW -->				13073		4534		2970		5493		4846		2965		1763		3043		306		DOUBLE M/V		1918		2950		1278		2290		525		229

						12720		6002		4681		6063		5161		0		1763		2941		254		PDCI BIPOLE		1616		2567		1237		2191		517		229

						13051		4649		3076		5362		4667		2965		1763		3042		308		PV-DEVERS		1775		2832		614		2012		463		220

						13085		4713		3151		5321		4488		2965		1763		3095		305		PV-N.GILA		1714		2425		992		2728		170		172

						14994		5692		4361		6011		5163		2965		1763		2960		265		2 SONGS		593		705		442		392		93		92

		Notes:

		1)  Adelanto SVC inserted

		2)  System Swing bus is Encina 5

		3)  SCE capacitors modeled as SVDs and allowed to float

		4)  SDG&E capacitors modeled as SVDs and allowed to float

		5)  IID 230/161 kV Transformer using 115% Emergency Rating per IID

		6)  Bypassed 1 SWPL capacitor to alleviate steady-state SWPL overload (In IV-NG @ NG)

		7)  Moved PST's at Perkins to 600 MW each bank to alleviate SWPL overload

		8)  4 - 480's and 2 - 320's beyond RMR in SCE

		*2 - 480's beyond RMR in SCE

		**1 - 480 beyond RMR In SCE

		***4 - 480's and 2 -320's beyond RMR in SCE





HS Summary - OTC

		2000 Summer EOR/SCIT Paths OTC Study Results

																										Var Margin (Mvar) Monitoring																		Stability

				Inertia		Flows																				Malin		Victor ville		Devers		Miraloma		Miguel		South Bay		Miguel		TJI		South Bay		Comments

		Case Description		MWs		SCIT		COI		P-26		WOR		EOR		PDCI		IPP		SDGE/CFE Import		SDGE-CFE		Contingency		500		500		500		500		500		69		230		230		138

		hs_s13_p29_m28_s2750_c300_swplcaps_2els				13025		4597		2803		5612		4948		2965		1763		3053		307

		Load + losses:				12819		5434		3822		6083		5215		2965		0		2988		273		IPP BIPOLE		985		3000		1316		2637		525		230		578		420		488		Stable

		PG&E:  20865 MW				12815		5453		3840		6062		5185		2965		0		2988		273		IPP - CRSTMC		969		3000		1313		2634		517		230		569		413		485		Stable

		SCE:  18047 MW				13101		4684		2899		5589		4890		2965		1763		3103		304		IV-MG RAS - TJI		1752		2558		1155		1590		203		159		258		164		267		Stable

		SDG&E:  3581 MW				13101		4711		2930		5557		4813		2965		1763		3103		304		IV - NGILA		1692		2486		1067		1629		249		205		272		232		336		Stable

		LADWP:  5475 MW				13023		4631		2837		5571		4938		2965		1763		3048		307		LUGO-ELD/MOH		1792		3000		1285		2563		512		227		558		407		476		Stable

		CFE:  1667 MW				13074		4551		2767		5696		5001		2965		1763		3051		306		DOUBLE M/V		1919		2979		1274		2379		512		228		564		411		479		Stable

						12723		6020		4474		6272		5319		0		1763		2948		253		PDCI BIPOLE		1615		2571		1228		2210		210		227		554		399		475		Stable

						13062		4668		2877		5570		4821		2965		1763		3050		308		PV-DEVERS		1762		2786		614		2010		447		214		474		326		414		Stable

						13094		4731		2952		5528		4649		2965		1763		3102		305		PV-N.GILA		1694		2491		969		1473		166		169		182		154		229		Stable

						14998		5710		4154		6220		5322		2965		1763		2968		265		2 SONGS		592		601		396		350		80		80		76		67		88		Stable

		hs_s13_p29_m28_s2145_c0_swplcaps*				13015		4613		2817		5586		4909		2965		1763		2145		5

																								IPP BIPOLE		885		2999		1235		2159		728		238		858		637		566

																								IPP - CRSTMC		850		2950		1226		2186		720		237		851		633		565

																								IV-MG RAS - TJI		1655		2372		1079		1849		255		204		374		229		394

																								IV - NGILA		1674		2427		1073		1799		398		225		542		449		499

																								LUGO-ELD/MOH		1801		2754		1176		2067		711		236		844		628		562

																								DOUBLE M/V		1896		2544		1194		2037		726		238		858		637		567

																								PDCI BIPOLE		1461		2378		1203		2016		717		237		846		628		563

																								PV-DEVERS		1755		2336		571		1712		730		219		767		554		515

																								PV-N.GILA		1674		2356		974		1737		360		223		449		374		447

																								2 SONGS		511		1273		853		856		436		209		409		352		383

		hs_s135_p29_m28_s2145_c0_swplcaps**				13495		4662		2873		6008		5296		2965		1763		2136		6

																								2 SONGS		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.

		hs_s135_p28_S2145_c0_swplcaps***				13499		4658		2868		6018		5276		2965		1763		2138		5

																								2 SONGS		-		1932		996		1320		441		206		418		357		389

		hs_s14_p28_S2145_c0_swplcaps***				13988		4715		2915		6460		5683		2965		1763		2137		6

																								2 SONGS		-		1744		944		1230		397		196		377		323		371

		hs_s15_p28_S2145_c0_swplcaps***				14986		4649		2858		7510		6606		2965		1763		2159		7

																								2 SONGS		-		1303		745		1032		328		199		313		270		343

		hs_s155_p28_S2145_c0_swplcaps***				15494		4678		2884		7990		7006		1884		1763		2130		7

																								2 SONGS		-		742		482		587		196		168		187		165		213

		hs_s16_p28_S2145_c0_swplcaps***				15927		4720		2912		8394		7369		2965		1763		2122		8

																								2 SONGS		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.

		hs_s13_p29_m28_s2545_c400_swplcaps				13021		4604		2808		5602		4942		2965		1763		2541		408

																								IPP BIPOLE		944		2963		1239		2145		613		237		712		505		554

																								IPP - CRSTMC		905		2922		1227		2112		616		236		703		497		551

																								IV-MG RAS - TJI		1788		2414		1124		1846		254		204		374		175		394

																								IV - NGILA		1708		2242		1010		1581		326		226		380		321		450

																								LUGO-ELD/MOH		1817		2765		1197		2069		605		235		691		491		548

																								DOUBLE M/V		1909		2545		1205		2034		620		237		708		502		553

																								PDCI BIPOLE		1523		2401		1203		2022		614		237		702		495		551

																								PV-DEVERS		1778		2328		572		1692		553		219		621		413		490

																								PV-N.GILA		1723		2211		918		1549		282		211		324		272		390

																								2 SONGS		503		946		692		609		284		205		272		237		296

		hs_s13_p29_m28_s2750_c300_swplcaps_2els_25L				13347		4637		2849		5886		5182		2965		1763		3054		307

		2.5% Flow Test				15308		5745		4194		6490		5555		2965		1763		2969		266		2 SONGS		-		354		-		-		-		53		48		43		58

		hs_s13_p29_m28_s2750_c300_swplcaps_2els_5L				13969		4695		2891		6454		5700		2965		1763		3053		308

		5% Flow Test				14038		4794		3001		6419		5632		2965		1763		3103		304		IV-MG RAS - TJI		-		2169		-		-		-		158		254		162		263

		Notes:

		1)  Adelanto SVC inserted

		2)  System Swing bus is Encina 5

		3)  SCE capacitors modeled as SVDs and allowed to float

		4)  SDG&E capacitors modeled as SVDs and allowed to float

		5)  IID 230/161 kV Transformer using 115% Emergency Rating per IID

		6)  Bypassed 1 SWPL capacitor to alleviate steady-state SWPL overload (In IV-NG @ NG)

		7)  Moved PST's at Perkins to 600 MW each bank to alleviate SWPL overload

		8)  4 - 480's and 2 - 320's beyond RMR in SCE

		*2 - 480's beyond RMR in SCE

		**1 - 480 beyond RMR In SCE

		***4 - 480's and 2 -320's beyond RMR in SCE





SHS Summary - OTC

		2000 Summer EOR/SCIT Paths OTC Study Results

																										Var Margin (Mvar) Monitoring																		Stability

				Inertia		Flows																				Malin		Victor ville		Devers		Miraloma		Miguel		South Bay		Miguel		TJI		South Bay		Comments

		Case Description		MWs		SCIT		COI		P-26		WOR		EOR		PDCI		IPP		SDGE/CFE Import		SDGE-CFE		Contingency		500		500		500		500		500		69		230		230		138

		shs1_s105_p29_m28_s2750_c300_swplcaps_alljets				10783		4770		2668		3604		3115		2966		1763		3059		310

		(Encina 5 not within reactive limits.)				10844		4530		2734		3597		3075		2966		1763		3107		308		IV-MG RAS - TJI		1938		2990		1310		1767		191		177		197		172		205		Stable

						12799		5604		4063		4222		3496		2966		1763		2961		270		2 SONGS		673		823		433		637		87		73		79		74		82		Stable

		Load + losses:				10608		5322		3701		4084		3386		2966		0		2988		277		IPP BIPOLE		1107		3000		1399		2624		639		251		680		514		566		Stable

		PG&E:    20857  MW				10606		5334		3722		4070		3366		2966		0		2987		277		IPP - CRSTMC		1089		3000		1406		2646		635		251		678		512		566		Stable

		SCE:  20418 MW				10852		4554		2763		3576		3009		2966		1763		3111		308		IV - NGILA		1892		2967		1212		1861		286		229		312		268		327		Stable

		SDG&E:  4341  MW				10778		4495		2693		3571		3107		2966		1763		3056		310		LUGO-ELD/MOH		2008		3000		1391		2658		652		249		703		529		583		Stable

		LADWP:  6128 MW				10825		4423		2631		3683		3164		2966		1763		3057		309		DOUBLE M/V		2102		3000		1369		2503		654		248		704		531		583		Stable

		CFE:  1668 MW				10627		5901		4356		4272		3490		0		1763		2948		263		PDCI BIPOLE		1747		3000		1337		2450		629		251		673		507		565		Stable

						10798		4506		2704		3581		3033		2966		1763		3050		311		PV-DEVERS		2005		3000		670		2197		675		242		691		499		564		Stable

						10848		4571		3780		3554		2831		2966		1763		3113		309		PV-N.GILA		1920		2897		1146		1614		193		194		206		182		225		Stable

						10830		4494		2706		3618		3164		2706		1763		3053		309		LUGO SOUTH DLO		1983		3000		1058		1342		594		242		638		481		560		Stable

						10806		4478		2684		3614		3160		2966		1763		3055		309		SERRANO NORTH DLO		2024		3000		1057		2415		611		245		665		501		571		Stable

		shs1_s105_p29_m28_s2650_c300_swplcaps_alljets				10782		4471		2669		3602		3110		2966		1763		2959		308

		(Encina 5 within reactive limits.)				12795		5603		4052		4219		3491		2966		1763		2861		266		2 SONGS		680		1169		1209		676		149		128		135		123		145

		shs1_s105_p29_m28_s2550_c400_swplcaps_alljets

																								2 SONGS

		Notes:

		1)  Adelanto SVC inserted

		2)  System Swing bus is Encina 5

		3)  SCE capacitors modeled as SVDs and allowed to float

		4)  SDG&E capacitors modeled as SVDs and allowed to float

		5)  IID 230/161 kV Transformer using 115% Emergency Rating per IID

		6)  Bypassed 1 SWPL capacitor to alleviate steady-state SWPL overload (In IV-NG @ NG)

		7)  Moved PST's at Perkins to 600 MW each bank to alleviate SWPL overload

		8) All SDG&E steam and jets on-line

		9)  All SCE steam and jets on-line





SHS Summary - 1

		2000 Summer EOR/SCIT Paths OTC Study Results

																										Var Margin (Mvar) Monitoring																				Stability

				Inertia		Flows																				Malin		Table Mt		Victor ville		Devers		Miraloma		Miguel		South Bay		Miguel		TJI		South Bay		Comments

		Case Description		MWs		SCIT		COI		P-26		WOR		EOR		PDCI		IPP		SDGE/CFE Import		SDGE-CFE		Contingency		500		500		500		500		500		500		69		230		230		138

		shs_s120_p29_m28_s2850_c0				11965		4583		2787		4664		4076		2966		1763		2853		0

						11694		5377		3758		5120		4334		2966		0		2778		-29		IPP BIPOLE		1099		1492		3000		1319		2622		826		251		807		615		534

						11691		5396		3776		5099		4300		2966		0		2778		-29		IPP - CRSTMC		1066		1460		3000		1319		2608		816		250		799		610		532

						12048		4680		2895		4636		4002		2966		1763		2914		13		IV-MG RAS - TJI		1728		2251		2711		1109		1418		187		170		193		239		198

						12017		4670		2883		4618		3946		2966		1763		2892		7		IV - NGILA		1750		2280		2896		1155		1932		407		238		535		455		485

		Load + losses:				11961		4612		2817		4628		4068		2966		1763		2849		9		LUGO-ELD/MOH		1906		2444		3000		1304		2576		844		249		837		640		557

		PG&E:    20857  MW				12031		4236		2808		4712		4118		2966		1763		2867		18		DOUBLE M/V		2407		2787		3000		1323		2541		859		250		849		649		560

		SCE:  20418 MW				11853		5939		4382		5300		4434		0		1763		2742		-48		PDCI BIPOLE		1748		1915		2841		1242		2322		840		249		824		627		554

		SDG&E:  4341  MW				11997		4648		2855		4626		3939		2966		1763		2852		10		PV-DEVERS		1884		2359		3000		648		2065		749		239		745		573		522

		LADWP:  6128 MW				12012		4683		2897		4599		3796		2966		1763		2890		7		PV-N.GILA		1775		2284		2930		1069		1914		376		244		464		396		450

		CFE:  1668 MW				13857		5639		4077		5255		4447		2966		1763		2768		-38		2 SONGS		729		1105		1224		751		705		226		142		193		178		174

																								LUGO SOUTH DLO		-		-		3000		939		1287		-		-		-		-		-

																								SERRANO NORTH DLO		-		-		3000		1240		2486		-		-		-		-		-

		shs_s125_p29_m28_s2850_c0				11965		4583		2787		4664		4076		2966		1763		2853		0

		*  Encina 5 Qmax is 201, limit is 168 MVAr				12587		4727		2945		5124		4438		2966		1763		2911		-36		IV - MG RAS - TJI		1666		2189		2386		1051		1398		186		169		191		237		197

						14350		5658		4094		5730		4879		2966		1763		2769		10		2 SONGS		710		1052		995		493		449		139		98*		118		110		110

		shs_s120_p29_m28_s2550_c200				11963		4586		2792		4658		4065		2966		1763		2543		209

						11701		5385		3768		5117		4325		2966		0		2476		174		IPP BIPOLE		1087		1484		3000		1325		2620		840		244		840		628		562

						11697		5404		3786		5095		4291		2966		0		2474		174		IPP - CRSTMC		1051		1408		3000		1309		2603		833		243		832		622		560

						12012		4653		2864		4632		4002		2966		1763		2581		208		IV-MG RAS - TJI		1784		2323		2970		1183		2111		230		183		289		235		291

						12010		4669		2882		4612		3938		2966		1763		2579		207		IV - NGILA		1763		2285		2915		1135		1972		377		236		448		385		435

		Load + losses:				11960		4615		2821		4622		4058		2966		1763		2540		209		LUGO-ELD/MOH		1848		2438		3000		1302		2558		830		242		828		622		559

		PG&E:    20857  MW				12028		4238		2811		4706		4107		2966		1763		2556		217		DOUBLE M/V		2405		2785		3000		1322		2525		837		243		839		630		562

		SCE:  20418 MW				11598		5951		4397		5300		4428		0		1763		2444		156		PDCI BIPOLE		1802		2013		2789		1231		2288		824		241		817		612		554

		SDG&E:  4341  MW				11996		4652		2860		4619		3926		2966		1763		2541		209		PV-DEVERS		1877		2351		3000		651		2045		735		253		745		564		528

		LADWP:  6128 MW				12008		4682		2896		4596		3792		2996		1763		2582		208		PV-N.GILA		1779		2290		2996		1093		1982		342		223		381		327		404

		CFE:  1668 MW				13855		5641		4080		5249		4438		2966		1763		2463		165		2 SONGS		729		1106		1576		926		913		308		169		264		239		245

		shs_s125_p29_m28_s2850_c0_1PVcap				11960		4590		2795		4652		4038		2966		1763		2767		-38

		1 Cap on PV-NG at NG Bypassed																						IV - MG RAS - TJI		1733		2259		2519		1111		1424		187		170		193		239		198

		Encina 5 Qmax is 215, limit is 168 MVAr																						2 SONGS		697		1035		527		348		286		95		69		85		91		77

		shs_s125_p29_m28_s2850_c0_pf985				11965		4583		2787		4664		4076		2966		1763		2853		10

		Encina 5 Qmax is 218, limit is 168 MVAr																						IV - MG RAS - TJI		1728		2250		1209		638		555		56		51		56		239		58

																								2 SONGS		727		1102		877		443		389		122		75		103		110		86

		Notes:

		1)  Adelanto SVC inserted

		2)  Encina 5 is swing bus

		3)  SCE capacitors modeled as SVDs

		4)  SDG&E capacitors modeled as SVDs

		5)  IID 230/161 kV Transformer at 100%.

		**  Bypassing more than 1 SWPL capacitor overloads south of SONGS (limit is 1800, actual 2000 MW)



&CDRAFT



HS Summary - 1

		2000 Summer EOR/SCIT Paths OTC Study Results

																										Var Margin (Mvar) Monitoring																				Stability

				Inertia		Flows																				Malin		Table Mt		Victor ville		Devers		Miraloma		Miguel		South Bay		Miguel		TJI		South Bay		Comments

		Case Description		MWs		SCIT		COI		P-26		WOR		EOR		PDCI		IPP		SDGE/CFE Import		SDGE-CFE		Contingency		500		500		500		500		500		500		69		230		230		138

		hs_s130_p29_m28_s2850_c0				12997		4649		2850		5411		4743		2965		1763		2857		4

																								IPP BIPOLE		867		1180		3000		1352		2861		756		223		775		573		539

																								IPP - CRSTMC		797		1141		3000		1358		2857		742		222		762		564		535

																								IV-MG RAS - TJI		1606		2050		2233		1106		1313		185		149		201		234		211

		Load + losses:																						IV - NGILA		1644		2109		2632		1123		1965		352		231		467		397		461

		PG&E:  20865 MW																						LUGO-ELD/MOH		1736		2290		3000		1353		2836		740		221		763		568		533

		SCE:  18047 MW																						DOUBLE M/V		1855		2312		2985		1336		2578		750		221		771		573		533

		SDG&E:  3581 MW																						PDCI BIPOLE		1542		1557		2488		1270		2275		726		239		741		548		526

		LADWP:  5475 MW																						PV-DEVERS		1727		2132		2916		629		2266		618		224		640		481		484

		CFE:  1667 MW																						PV-N.GILA		1646		2088		2625		1037		1885		321		214		393		334		420

																								2 SONGS		423		664		1382		833		800		204		145		179		159		195

		hs_s135_p29_m28_s2850_c0				13505		4685		2883		5885		5143		2965		1763		2859		5

																								IV-MG RAS - TJI		1552		1966		2148		1052		1455		188		150		210		233		218

																								2 SONGS		377		551		1013		670		613		154		131		136		120		150

		hs_s140_p29_m28_s2850_c0				14009		4716		2916		6355		5562		2965		1763		2846		5

																								IV-MG RAS - TJI		1460		1866		1852		893		1128		187		150		205		229		215

																								2 SONGS		315		453		1045		691		710		194		161		174		155		197

		hs_s145_p29_m28_s2850_c0				14505		4744		2952		6812		5957		2965		1763		2860		6

																								IV-MG RAS - TJI		1334		1741		1083		691		685		149		140		152		224		161

																								2 SONGS		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.		No Sol.

		hs_s130_p29_m28_s2550_c200				12998		4651		2852		5409		4739		2965		1763		2559		209

																								IPP BIPOLE		837		1176		3000		1366		2940		785		241		828		603		579

																								IPP - CRSTMC		793		1128		3000		1360		2895		773		239		814		595		575

																								IV-MG RAS - TJI		1687		2150		2804		1189		2171		233		187		303		235		327

		Load + losses:																						IV - NGILA		1654		2115		2724		1150		2172		358		217		445		379		467

		PG&E:  20865 MW																						LUGO-ELD/MOH		1785		2284		3000		1358		2880		768		239		815		595		574

		SCE:  18047 MW																						DOUBLE M/V		1852		2308		3000		1338		2617		777		239		820		600		574

		SDG&E:  3581 MW																						PDCI BIPOLE		1419		1571		2514		1283		2303		760		238		797		581		566

		LADWP:  5475 MW																						PV-DEVERS		1723		2196		2933		632		2302		652		225		700		517		529

		CFE:  1667 MW																						PV-N.GILA		1664		2101		2737		1064		2095		327		224		375		319		430

																								2 SONGS		458		690		1981		1089		1341		367		204		333		286		343

		Notes:

		1)  Adelanto SVC inserted



&CDRAFT



SDGE-CFE Nomogram

		0

		2550

		2750

		2750

		0



TO
 
CFE

TO
 
SDGE

SDG&E Imports (MW)

Path 45 (CFE)

SDG&E/CFE IMPORT NOMOGRAM

408

408

300

-408

-408



SDGE-CFE Data Points

		0		408

		2550		408

		2750		300

		2750		-408

		0		-408






_1027927294.xls
AC-DC-Heavy Summer - OTC

																										POST-TRANSIENT																																TRANSIENT STABILITY

																										MVAR MARGIN																														VOLT. DIP		NEWELL 69 VOLTAGE (%)

		% N. Cal. Hydro		Description		AC+  DC		AC+NCH		COI		PDCI (P.O.)		M/V		MP-SL    FLOW		NE/SE FLOW		NJD		RATS		SCIT		2 PV             (BPA)		2 PV (PG&E)		2   DC  PP		2 ML  PP		2 P  PP		DC                (BPA)		DC (PG&E)		MAS DLO		RMS DLO		TMS   DLO		TSN  DLO		TSTR-TRLB		MV DLO		OLTR SLO		CJOL SLO		1-PV		2 PALO VERDE          w/ FT. ROCK

		55%		hs_c46_p29_h55_m28_ms4_s12  (Nomogram Point)		7578		6840.5		4613		2965		2791		426		1160		7699		-2		12152		212 - GR		281 - RM		697 - OS		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		1 - < 10%		13%		0 Cycles

		55%		5% COI Test		7667		6929.5		4702		2965		2778		424		1174		7784		-2		12151		7- GR		21 - RM		-		-		-		-		-		-		-		-		-		-		-		-		-

		55%		2.5% COI Test		0		2227.5		0																				-		-		-		-		-		-		-		-		-		-		-		-		-

		55%		100 MW Stability Test		0		0																																																		14%		0 Cycles

		60%		hs_c46_p29_h60_m28_ms4_s12		7567		7032		4602		2965		2781		418		1171		7695		-1		12152		174 - GR		255 - RM		642 - DX		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000

		60%		hs_c455_p29_h60_m28_ms4_s12 (Nomogram Point)		7521		6986		4556		2965		2809		420		1166		7701		-1		12174		234 - OS		319 - RM																												1 - < 10%

		70%		hs_c45_p29_h70_m28_ms4_s12		7471		7341		4506		2965		2811		403		1193		7716		-1		12200		204 - GR		267 - RM		680 - DX		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000

		70%		hs_c445_p29_h70_m28_ms4_s12 (Nomogram Point)		7418		7288		4453		2965		2801		407		1184		7714		-1		12182		276 - OS		379 - RM																												1 - < 10%

		80%		hs_c44_p29_h80_m28_ms4_s12		7363		7638		4398		2965		2805		384		1211		7704		5		12210		140 - GR		199 - RM		651 - DX		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000

		80%		hs_c43_p29_h80_m28_ms4_s12 (Nomogram Point)		7269		7544		4304		2965		2805		389		1196		7700		5		12197		275 - CJ		376 - RM																												1 - < 10%

		80%		hs_c43_p29_h80_m30_ms4_s12 (Nomogram Point)		7258		7533		4293		2965		2994		378		1207		7697		4		12395		281 - GR		413 - RM		-		-		-		> 1000		> 1000		-		-		-		-		-		-		-		-

		80%		hs_c43_p29_h80_m28_ms0_s12  (MP-SL Test)		7273		7548		4308		2965		2859		46		1012		7581		5		11892		138 - OS		211 - RM		-		-		-		-		-		-		-		-		-		-		-		-		-

		80%		hs_c42_p29_h80_m28_ms0_s13  (MP-SL Test)		7173		7448		4208		2965		2863		47		1006		7605		5		11892		252 - CJ		358 - RM		-		-		-		-		-		-		-		-		-		-		-		-		-

		90%		hs_c43_p29_h90_m28_ms4_s12		7270		7950		4305		2965		2811		374		1226		7712		2		12230		151 - GR		200 - RM		665 - DX		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000

		90%		hs_c42_p29_h90_m28_ms4_s12 (Nomogram Point)		7173		7853		4208		2965		2802		380		1210		7701		2		12207		281 - GR		401 - RM																												1 - < 10%

		100%		hs_c42_p29_h100_m28_ms4_s12		7162		8247		4197		2965		2804		366		1224		7706		9		12220		83 - HF		44 - RM		628 - GR		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000

		100%		hs_c40_p29_h100_m28_ms4_s12 (Nomogram Point)		6973		8058		4008		2965		2812		370		1206		7700		9		12213		208 - GR		305 - RM																												1 - < 10%

		* Lower Columbia generation includes: The Dalles, John Day, Bonneville, and McNary.

		** 230 kV Capacitors at Vaca-Dixon, Tesla, and Metcalf were switched in as well as 132 MVAr SVC at Adelanto 500 kV in the post-transient routine.



&C&"Times New Roman,Bold" 2000 Summer AC/DC Nomogram
Post-Transient/Transient Stability Summary

&R&F &D
MCW



AC-DC-Heavy Summer

																										POST-TRANSIENT																																		TRANSIENT STABILITY

																										MVAR MARGIN																																VOLT. DIP		NEWELL 69 VOLTAGE (%)

		% N. Cal. Hydro		Description		AC+  DC		AC+NCH		COI		PDCI (P.O.)		M/V		MP-SL    FLOW		NE/SE FLOW		NJD		RATS		SCIT		2 PV             (BPA)		2 PV (PG&E)		2   DC  PP		2 ML  PP		2 P  PP		DC                (BPA)		DC (PG&E)		MAS DLO		RMS DLO		TMS   DLO		TSN  DLO		TSTR-TRLB		MV DLO		LBN DLO		OLTR SLO		CJOL SLO		1-PV		2 PALO VERDE          w/ FT. ROCK

		55%		hs_c46_p29_h55_m28_ms4_s12  (Nomogram Point)		7578		6840.5		4613		2965		2791		426		1160		7699		-2		12152		212 - GR		281 - RM		697 - OS		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		--		> 1000		> 1000		1 - < 10%

		55%		5% COI Test		7667		6929.5		4702		2965		2778		424		1174		7784		-2		12151		7- GR		21 - RM		-		-		-		-		-		-		-		-		-		-		-		-		-		-

		55%		2.5% COI Test		0		0

		55%		100 MW Stability Test		0		0

		60%		hs_c46_p29_h60_m28_ms4_s12		7567		7032		4602		2965		2781		418		1171		7695		-1		12152		174 - GR		255 - RM		642 - DX		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		--		> 1000		> 1000

		60%		hs_c455_p29_h60_m28_ms4_s12 (Nomogram Point)		7521		6986		4556		2965		2809		420		1166		7701		-1		12174		234 - OS		319 - RM																														1 - < 10%

		60%		5% COI Test		0		0

		60%		2.5% COI Test		0		0

		60%		100 MW Stability Test		0		0

		70%		hs_c45_p29_h70_m28_ms4_s12		7471		7341		4506		2965		2811		403		1193		7716		-1		12200		204 - GR		267 - RM		680 - DX		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		--		> 1000		> 1000

		70%		hs_c445_p29_h70_m28_ms4_s12 (Nomogram Point)		7418		7288		4453		2965		2801		407		1184		7714		-1		12182		276 - OS		379 - RM																														1 - < 10%

		70%		5% COI Test		0		0

		70%		2.5% COI Test		0		0

		70%		100 MW Stability Test		0		0

		80%		hs_c44_p29_h80_m28_ms4_s12		7363		7638		4398		2965		2805		384		1211		7704		5		12210		140 - GR		199 - RM		651 - DX		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		--		> 1000		> 1000

		80%		hs_c43_p29_h80_m28_ms4_s12 (Nomogram Point)		7269		7544		4304		2965		2805		389		1196		7700		5		12197		275 - CJ		376 - RM																														1 - < 10%

		80%		5% COI Test		0		0

		80%		2.5% COI Test		0		0

		80%		100 MW Stability Test		0		0

		90%		hs_c43_p29_h90_m28_ms4_s12		7270		7950		4305		2965		2811		374		1226		7712		2		12230		151 - GR		200 - RM		665 - DX		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		--		> 1000		> 1000

		90%		hs_c42_p29_h90_m28_ms4_s12 (Nomogram Point)		7173		7853		4208		2965		2802		380		1210		7701		2		12207		281 - GR		401 - RM																														1 - < 10%

		90%		5% COI Test		0		0

		90%		2.5% COI Test		0		0

		90%		100 MW Stability Test		0		0

		100%		hs_c42_p29_h100_m28_ms4_s12		7162		8247		4197		2965		2804		366		1224		7706		9		12220		83 - HF		44 - RM		628 - GR		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		> 1000		--		> 1000		> 1000

		100%		hs_c40_p29_h100_m28_ms4_s12		6973		8058		4008		2965		2812		370		1206		7700		9		12213		208 - GR		305 - RM																														1 - < 10%

		100%		5% COI Test		0		0

		100%		2.5% COI Test		0		0

		100%		100 MW Stability Test		0		0

		70%		hs_c46_p29_h60_m28_ms4_s12		0		2835

		70%		5% COI Test		0		2835

		70%		2.5% COI Test		0		2835

		70%		100 MW Stability Test		0		2835

		80%		hs_c46_p29_h60_m28_ms4_s12		0		3240

		80%		5% COI Test		0		3240

		80%		2.5% COI Test		0		3240

		80%		100 MW Stability Test		0		3240

		90%		hs_c46_p29_h60_m28_ms4_s12		0		3645

		90%		5% COI Test		0		3645

		90%		2.5% COI Test		0		3645

		90%		100 MW Stability Test		0		3645

		100%		hs_c46_p29_h60_m28_ms4_s12		0		4050

		100%		5% COI Test		0		0

		100%		2.5% COI Test		0		4050

		100%		100 MW Stability Test		0		4050

		* Lower Columbia generation includes: The Dalles, John Day, Bonneville, and McNary.

		** 230 kV Capacitors at Vaca-Dixon, Tesla, and Metcalf were switchin in as well as 132 MVAr SVC at Adelanto 500 kV in the post-transient routine.



&C&"Times New Roman,Bold" 2000 Summer AC/DC Nomogram
Post-Transient/Transient Stability Summary

&R&F &D
MCW



AC-DC HS Nomogram

		3000		3000		3000		3000		3000		3000

		4600		4600		4600		4600		4600		4600

		4600		4600		4600		4600		4600		4600

		4550		4550		4550		4550		4550		4550

		4550		4550		4550		4550		4550		4550

		4450		4450		4450		4450		4450		4450

		4450		4450		4450		4450		4450		4450

		4300		4300		4300		4300		4300		4300

		4300		4300		4300		4300		4300		4300

		4200		4200		4200		4200		4200		4200

		4200		4200		4200		4200		4200		4200

										0

		4000		4000		4000		4000		4000		4000

		4000		4000		4000		4000		4000		4000



N. Cal. Hydro

55%

60%

70%

80%

90%

100%

COI/NW-Sierra (MW)

PDCI Flow @ Celilo (MW)

2000 HEAVY SUMMER AC/DC NOMOGRAM
(As a function of the percentage of Northern California Hydro Generation)
(For Northern California area load less than 20,850 MW)

2975

2975

2000

2975

2000

2975

2000

2975

2000

2975

2000

2975

2000



AC-DC Nomogram HS Data

		3000		2975

		4600		2975

		4600		2000

		4550				2975

		4550				2000

		4450						2975

		4450						2000

		4300								2975

		4300								2000

		4200										2975

		4200										2000

		4000												2975

		4000												2000





AC-DC-Super Heavy Summer

																										POST-TRANSIENT																																		TRANSIENT STABILITY

																										MVAR MARGIN																																VOLT. DIP		NEWELL 69 VOLTAGE (%)

		% N. Cal. Hydro		Description		AC+  DC		AC+NCH		COI		PDCI (P.O.)		M/V		MP-SL    FLOW		NE/SE FLOW		NJD		RATS		SCIT		2 PV-BPA		2 PV-PGE		2   DC  PP		2 ML  PP		2 P  PP		DC-BPA		DC-PGE		MAS DLO		RMS DLO		TMS DLO		TSN   DLO		TSTR-TRLB   DLO		MV DLO		TSTR SLO		OLTR SLO		CJOL SLO		1-PV		2 PALO VERDE          w/ FT. ROCK

		60%		shs_c42_p26_h60_m0_ms-3_s8		6870		6645		4215		2655		-56		-296		-162		7798		-3		8403		585 - MA		471 - MT		654 - MT		No Sol.		199 - MT		1377 - MA		810 - MT		639 - MT		240 - MT		190 - MT		690 - MT		-		466 - MT		-		388 - MT		765 - MT

		60%		shs_c42_p26_h60_m0_ms-3_s8_sfjets (Nomogram Point)		6866		6641		4211		2655		-60		-299		-157		7796		-3		8403		-		-		-		219 - MT		433 - MT		-		-		-		461 - MT		416 - MT		-		485 - MT		-		-		594 - MT		-

		60%		shs_c42_p26_h60_m0_ms-3_s8_sfjets (RND1)		6871		6646		4216		2655		-57		-304		-161		7799		-3		8404		794 - CJ		879 - MT		-		399 - MT												504 - MT

		60%		shs_c43_p26_h60_m0_ms-3_s8_sfjets (RND1)		6949		6724		4294		2655		24		-306		-141		7875		-3		8503		676 - MA		750 - RM		-		379 - MT		-		-		-		-		-		475 - MT		-		-		-		-		-

		60%		shs_c44_p26_h60_m0_ms-3_s8_sfjets (RND1)                                          (Revised Nomogram Point)		7058		6833		4403		2655		135		-304		-113		7982		-3		8642		412 - CJ		479 - TM		-		322 - MT		-		-		-		-		-		359 - MT		-		-		-		-		-		-

		60%		shs_c42_p26_h60_m0_ms-3_s8  (Reduced Bay Load to 8600)		6854		6629		4199		2655		-74		-307		-144		7793		-3		8403		-		-		-		-		-		-		-		-		-		-		-		-		-		-		-		-

		60%		shs_c415_p26_h60_m0_ms-3_s8		6809		6584		4154		2655		-46		-294		-172		7797		-3		8404		-		-		-		-		-		-		-		-		-		-		-		-		-		*739 - MT		-		-

		60%		5% COI Test		0		2430		0

		60%		2.5% COI Test		0		2430		0

		60%		100 MW Stability Test		0		2430		0

		70%		shs_c41_p26_h70_m0_ms-3_s8_sfjets		6758		6938		4103		2655		-73		-310		-145		7791		-3		8403		572 - MA		434 - MT		622 - MT		No Sol.		222 - MT		1350 - CJ		783 - MT		739 - MT		256 - MT		142 - MT		977 - MT		-		484 - MT		-		380 - MT		773 - MT

		70%		shs_c41_p26_h70_m0_ms-3_s9_sfjets (Nomogram Point)		6754		6934		4099		2655		-78		-313		-140		7790		-3		8403		-		-		-		218 - MT		442 - MT		-		-		-		450 - MT		361 - MT		-		488 - MT		-		-		568 - MT		-

		70%		shs_c41_p26_h70_m0_ms-3_s8_sfjets (RND1)		6759		6939		4104		2655		-74		-318		-144		7792		-3		8403		823 - CJ		845 - MT		-		424 - MT		-		-		-		-		-		461 - MT		-		-		-		-		-		-

		70%		shs_c42_p26_h70_m0_ms-3_s8_sfjets (RND1)		6837		7017		4182		2655		6		-315		-124		7868		-3		8503		681 - MA		764 - MT		-		383 - MT		-		-		-		-		-		421 - MT		-		-		-		-		-		-

		70%		shs_c43_p26_h70_m0_ms-3_s8_sfjets (RND1)                                            (Revised Nomogram Point)		6955		7135		4300		2655		126		-318		-94		7983		-3		8634		357 - CJ		451 - RM		-		327 - MT		-		-		-		-		-		434 - MT		-		-		-		-		-		-

		70%		shs_c40_p26_h70_m0_ms-3_s8		6661		6841		4006		2655		-57		-307		-160		7797		-3		8404		-		-		-		-		-		-		-		-		-		-		-		-		-		*770 - MT		-		-

		80%		shs_c40_p26_h80_m0_ms-3_s8		6653		7238		3998		2655		-94		-323		-124		7807		-3		8403		474 - CJ		368 - MT		527 - MT		No Sol.		188 - MT		1199 - MA		687 - MT		763 - MT		224 - MT		28 - MT		685 - MT		-		439 - MT		-		300 - MT		723 - MT

		80%		shs_c40_p26_h80_m0_ms-3_s9_sfjets		6649		7234		3994		2655		-99		-326		-119		7806		-3		8403		-		-		-		148 - MT		395 - MT		-		-		-		396 - MT		233 - MT		-		420 - MT		-		-		500 - MT		-

		80%		shs_c40_p26_h80_m0_ms-3_s8_sfjets (RND1)		6654		7239		3999		2655		-95		-331		-123		7809		-3		8403		819 - MA		748 - MT		-		367 - MT		-		-		-		-		-		362 - MT		-		-		-		-		-		-

		80%		shs_c41_p26_h80_m0_ms-3_s8_sfjets (RND1)                                                (Revised Nomogram Point)		6760		7345		4105		2655		13		-328		-96		7912		-3		8537		541 - CJ		570 - OL		-		306 - MT		-		-		-		-		-		288 - MT		-		-		-		-		-		-

		80%		shs_c39_p26_h80_m0_ms-3_s9_sfjets  (Nomogram Point)		6564		7149		3909		2655		-85		-324		-133		7792		-3		8403		-		-		-		200 - MT		-		-		-		-		-		301 - MT		-		-		-		-		540 - MT		-

		80%		shs_c38_p26_h80_m0_ms-3_s8		6458		7043		3803		2655		-63		-318		-154		7812		-3		8403		-		-		-		-		-		-		-		-		-		-		-		-		-		*788 - MT		-		-

		90%		shs_c39_p26_h90_m0_ms-3_s8		6621		7611		3966		2655		116		-342		-85		7797		-3		8651		356 - MA		277 - MT		461 - MT		No Sol.		174 - MT		1079 - MA		598 - MT		805 - MT		294 - MT		No Sol.		669 - MT		-		452 - MT		-		261 - MT		714 - MT

		90%		shs_c39_p26_h90_m0_ms-3_s9_sfjets		6613		7603		3958		2655		207		-347		-76		7795		-3		8751		-		-		-		140 - MT		407 - MT		-		-		-		475 - MT		148 - MT		-		404 - MT		-		-		470 - MT		-

		90%		shs_c39_p26_h90_m0_ms-3_s8_sfjets (RND1)                                                         (Revised Nomogram Point)		6618		7608		3963		2655		211		-353		-80		7797		-3		8751		746 - CJ		664 - MT		-		357 - MT		-		-		-		-		-		294 - MT		-		-		-		-		-		-

		90%		shs_c37_p26_h90_m0_ms-3_s9_sfjets  (Nomogram Point)		6370		7360		3715		2655		-16		-332		-127		7808		-3		8478		-		-		-		250 - MT		-		-		-		-		-		248 - MT		-		-		-		-		582 - MT		-

		90%		shs_c36_p26_h90_m0_ms-3_s8		6365		7355		3710		2655		155		-334		-123		7802		-3		8652		-		-		-		-		-		-		-		-		-		-		-		-		-		*790 - MT		-		-

		100%		shs_c38_p26_h100_m0_ms-3_s8		6506		7901		3851		2655		299		-356		-67		7798		-1		8851		196 - MA		168 - VD		392 - MT		No Sol.		143 - MT		919 - MA		509 - MT		804 - MT		265 - MT		No Sol.		635 - MT		-		403 - MT		-		178 - MT		700 - MT

		100%		shs_c37_p26_h100_m0_ms-3_s9_sfjets		6417		7812		3762		2655		307		-356		-76		7815		-1		8851		542 - CJ		425 - MT		-		137 - MT		407 - MT		-		-		-		511 - MT		158 - MT		-		391 - MT		-		-		447 - MT		-

		100%		shs_c37_p26_h100_m0_ms-3_s8_sfjets (RND1)                                                                       (Revised Nomogram Point)		6421		7816		3766		2655		309		-361		-78		7816		-1		8851		641 - CJ		605 - MT		-		319 - MT		-		-		-		-		-		262 - MT		-		-		-		-		-		-

		100%		shs_c36_p26_h100_m0_ms-3_s9_sfjets		6313		7708		3658		2655		322		-353		-90		7799		-3		8851		-		-		-		173 - MT		-		-		-		-		-		219 - MT		-		-		-		-		475 - MT		-

		100%		shs_c35_p26_h100_m0_ms-3_s9_sfjets  (Nomogram Point)		6228		7623		3573		2655		335		-351		-104		7802		-3		8851		-		-		-		223 - MT		-		-		-		-		-		-		-		-		-		-		534 - MT		-

		100%		shs_c34_p26_h100_m0_ms-3_s8		6063		7458		3408		2655		365		-343		-133		7809		-1		8852		-		-		-		-		-		-		-		-		-		-		-		-		-		*823 - MT		-		-

		*  The Tracy Transformer steady state at 888 MVA, overloads to 1224 MVA post-contingency; 840 MVA normal, and 1050 MVA emergency ratings.

		** 230 kV Capacitors at Vaca-Dixon, Tesla, and Metcalf were switchin in as well as 132 MVAr SVC at Adelanto 500 kV in the post-transient routine.

		3 of 4 S.F. Jets assumed on-line

		Moving the swing bus to Pittsburg 7 did not help for the loss of Moss Landing G-2



&C&"Times New Roman,Bold" 2000 Summer AC/DC Nomogram
Post-Transient/Transient Stability Summary

&R&F &D
MCW



AC-DC SHS Nomogram

		3000		3000		3000		3000		3000

		4200		4200		4200		4200		4200

		4200		4200		4200		4200		4200

		4100		4100		4100		4100		4100

		4100		4100		4100		4100		4100

		3900		3900		3900		3900		3900

		3900		3900		3900		3900		3900

		3715		3715		3715		3715		3715

		3715		3715		3715		3715		3715

		3575		3575		3575		3575		3575

		3575		3575		3575		3575		3575



N. Cal. Hydro

60%

70%

80%

90%

100%

COI/NW-Sierra (MW)

PDCI Flow @ Celilo (MW)

2000 SUPER HEAVY SUMMER AC/DC NOMOGRAM 
(As a function of the percentage of Northern California Hydro Generation) 
(For Northern California area load greater than 20,850 MW)

2965

2965

2000

2965

2000

2965

2000

2965

2000

2965

2000



AC-DC Nomogram SHS Data

		3000		2965

		4200		2965

		4200		2000

		4100				2965

		4100				2000

		3900						2965

		3900						2000

		3715								2965

		3715								2000

		3575										2965

		3575										2000





AC-DC SHS Nomogram-RND1

		3000		3000		3000		3000		3000

		4400		4400		4400		4400		4400

		4400		4400		4400		4400		4400

		4300		4300		4300		4300		4300

		4300		4300		4300		4300		4300

		4100		4100		4100		4100		4100

		4100		4100		4100		4100		4100

		3950		3950		3950		3950		3950

		3950		3950		3950		3950		3950

		3750		3750		3750		3750		3750

		3750		3750		3750		3750		3750



N. Cal. Hydro

60%

70%

80%

90%

100%

COI/NW-Sierra (MW)

PDCI Flow @ Celilo (MW)

2000 SUPER HEAVY SUMMER AC/DC NOMOGRAM 
(As a function of the percentage of Northern California Hydro Generation) 
(For Northern California area load greater than 20,850 MW)

2965

2965

2000

2965

2000

2965

2000

2965

2000

2965

2000



AC-DC Nomogram SHS Data-RND1

		3000		2965

		4400		2965

		4400		2000

		4300				2965

		4300				2000

		4100						2965

		4100						2000

		3950								2965

		3950								2000

		3750										2965

		3750										2000






_1017213870.doc
[image: image1.bmp][image: image2.png]





California EHV Transmission System











Encina







SONGS







Note: Also part







of Path 46







Control







Craig View







Weed







Junction







PIT River







  (Hydro)







Mission







Imperial Valley







Adelanto







Miguel







Palo







Verde







Devers







Valley







Serrano







Mira Loma







Lugo







Victorville







Rinaldi







Mohave







Eldorado







Mc Cullough







Market Place







Toluca







Midway







Diablo Canyon







Gates







Los







Banos







Sylmar







Intermountain







Celilo







Malin







Captain Jack







Southbay







Tesla







Metcalf







Moss







Landing







Tracy







Vaca



Dixon











Table



Mountain











Round



Mountain











Olinda







McCall







Panoche







Morro Bay







Helms







Santiago







Chino







CFE







CFE







Talega







Escondido







Mead







El Centro







Mirage







Coachella







West of River







Vincent







Feather River







     (Hydro)







Shasta







Keswick







Geysers







Hunters Point







Protrero







Pittsburg







San Luis







Big Creek







   (Hydro)







Kings River







Castaic







Cascade







Meridian







Drum







Summit







Inyo







Silver Peak







Transfer Paths/Rating















2000 Summer OTC







Path 15















North /South:







  Limited by Path 26 flow







South / North 







 3450MW







Path 26







3000MW  N/S







 2800MW







Path 27







1920MW E/W











 Limited by SCIT Total







Path 44







1800MW N-S











 Limited by Total Import to



 SDG&E and CFE







Path 45







408 MW Bi-directional 







 Limited by Total Import to



 SDG&E and CFE







Path 46







10,118 MW E/W







Limited by SCIT Total







Path 49







7550MW E/W







Limited by SCIT Total







Path 65







3100 N/S 



















3100MW







(PDCI)







Path 66







4800MW N/S    







 4600MW











(COI)







SCIT







18860 MW











13,000MW







Hoover







Colorado River







Contra







Costa







MEXICO







USA







Colorado River











(Path 65)















(







Path 66)











Stability







(Path 25)



















(Path 24)















(Path 60)







(Path 46)







(Path 61)







(Path 49)







(Path 43)







(Path 26)







(Path 42)







(Path 15)







  Stability























Thermal







































































Note: Also part







of Path 46







































East of River







USF Path 21







































(Path 27)







(Path 44)







(Path 41)







(Path 45)







Gregg







Bellota







Hyatt (CDWR)







Aqueduct







Mandaly







Ormond Beach







Pardee







Huntington







Beach







Newark







Navajo







Moenkopi







Liberty







Perkins







North







Gila







Maxwell



(WAPA)
















