Revised:  April 12, 2001

Minutes of PG&E Electric Transmission Grid Expansion Plan Meeting #3


[image: image1.png]Pacific Gas and
.3 Electric Company.

WE DELIVER ENERGY"




Pacific Gas and Electric Company

Electric Transmission Grid Expansion Plan 

For the Years 2002-2006 

Minutes of Meeting #3

Monday, April 2, 2001

San Francisco, CA
Meeting Attendees

	Name
	Organization
	Address
	Phone
	E-mail

	Ante, Jesse
	CPUC
	505 Van Ness Ave                San Francisco, CA  94102
	415-703-2820
	

	Casuncad, Dave
	PG&E
	245 Market Street - Rm317A

San Francisco, CA 94155
	415-973-1327
	drcl@pge.com

	Dowers, Danielle 
	Hetch-Hetchy
	1155 Market Street, 4th Floor

San Francisco, CA  94103
	415-554-3178
	ddowers@puc.sf.ca.us

	Esguerra, Mark
	PG&E


	245 - Market 3rd Floor                        San Francisco, CA   94155
	415-973-4380
	pme8@pge.com

	Flynn, Barry
	Flynn Associates
	4200 Driftwood Place                                        Discovery Bay, CA 94514
	925-634-7500
	brflynn@pacbell.net

	Hunt, Randall
	California ISO
	151 Blue Ravine Rd.                       Folsom, CA  95630
	916-351-4426
	Rhunt@caiso.com

	Keller, Mike
	Silicon Valley Power
	1500 Warburton Ave

Santa Clara, CA
	408-261-5470
	mkeller@ci.santa-clara.ca.us

	Kozminski, Kevin
	PG&E
	245 Market Street, Rm 330 F

San Francisco, CA
	415-973-5352
	KCK1@pge.com

	Langenberg, Joe
	CCP
	516 N.Shaw Suite 200                      Fresno, CA  93704
	559-260-9507
	-

	Law, Eric
	PG&E
	77 Beale St.   B15A
	415-973-7628
	ETL1@pge.com

	Lee, Kelly
	CPUC/ORA
	505 Van Ness Ave

SF, CA
	415-703-1795
	KCL@cpuc.ca.gov

	Magee, Charles
	CPUC
	505 Van Ness Ave

SF, CA
	415-703-4683
	

	Marcus, David
	CCUE
	P.O. Box 1287

Berkeley, CA  9470
	510-528-0228
	dmarcus@slip.net

	Meredith, Monte
	PG&E
	245 - Market 3rd Floor                        San Francisco, CA   94155
	415 973-2389
	MSMc@pge.com

	Micsa, Catalin
	California ISO
	151 Blue Ravine Rd.                       Folsom, CA  95630
	916-608-5704
	Cmicsa@caiso.com

	Mukherjee, Shishir
	City of 

Palo Alto
	250 Hamilton Ave                Palo Alto, CA  94301
	650-329-2537
	Shishir_mukherjee@city.palo-alto.ca.us

	Palisoc, Rod
	WAPA
	114 Parkshore Dr.         Folsom, CA  95630
	916-353-4557
	palisoc@wapa.gov

	Pereira, Les
	NCPA
	180 Cirby Way

Roseville, CA  95678
	916-781-4218
	Les@ncpa.com

	Rios, Marco
	PG&E
	245 Market Street, Rm 313C

San Francisco, CA  
	415-973-8460
	M1R9@pge.com

	Sparks, Robert
	California ISO
	151 Blue Ravine Rd.                       Folsom, CA  95630


	916-351-2198
	RSparks@caiso.com

	Tang, Clayton
	CPUC
	505 Van Ness Ave

SF, CA
	415-973-1823
	

	Thompson, Lorenzo
	PG&E
	245 - Market 3rd Floor                        San Francisco, CA   94155
	415-973-0539
	LJT7@pge.com

	Thomson, Chad
	PG&E
	245 - Market 3rd Floor                        San Francisco, CA   94155
	415-973-2635
	cet7@pge.com

	Tobias, Larry
	California ISO
	151 Blue Ravine Rd.                       Folsom, CA  95630
	916-608-5763
	LTobias@caiso.com

	Vijayraghavan, Bangalore
	PG&E
	245 Market Street 

Office 318 A

San Francisco, CA 94155
	415-973-2842
	BxV6@pge.com

	Wheatland, Gregg
	CCSF
	City Hall,

SF, CA  94102
	415-554-6780
	Gregg_Wheatland@ci.sf.ca.us

	Wood, Dan
	USE
	2108 Marchita Way                        Carmichael, CA  95608
	916-564-9663
	danwooduse@aol.com

	Wu, Tim
	LADWP
	111 N. Hope Street   Los Angeles, CA 90012
	213-367-0650
	ctwu@ladwp.com

	Yeo, Michael
	CPUC
	505 Van Ness Avenue                    San Francisco, CA 94105
	415-703-2719
	mey@cpuc.ca.gov


Attachments

1. Email (dated April 9, 2001) from Les Pereira of NCPA to PG&E, ISO and Stakeholders

2. PG&E Response to Les Pereira’s comments

Action Items from Meeting #3

Expansion Plan Update

1. Stakeholders have requested additional project information which will be provided either offline or through email. Les Pereira of NCPA requested additional information on the Bay Area Reactive Support Project.

Bay Area 2002 Load Serving Capability Study
2. Barry Flynn of Flynn Associates suggested reviewing the assumptions made for the online Bay Area generation and its consistency. Also suggested to verify the COI import level is set at a conservative level.

3. Les Pereira suggested PG&E coordinate with Operations and ISO in determining the Under Voltage Relay Setting and Load Shedding Scheme.

4. Provide base cases on ISO website.

Bay Area Bulk Transmission Import Study Update

5. Barry Flynn suggested PG&E add a column for CEC Status in the generation table.

6. Send base cases to ISO web site for comments.

7. Provide list of proposed bay area generation projects.

San Jose Long-Term Project

8. Dan Wood of USE suggested an additional C-3 contingency involving the loss of parallel 500 kV lines into the bay area (not on same tower).

9. General comment regards verifying that the back-ties for each subsystem be sized to 60-70% of its peak pocket load.

Greater Fresno Long-Term Assessment

10. Stakeholders suggested looking into any known environmental issues on the Gates-Gregg circuit alternative.

11. Provide list of proposed Fresno area generation projects.

Yuba and Sutter Counties Long-Term Transmission

ISO will provide comments and recommendations on study alternatives.

Humboldt Stability Study

12. ISO suggested a long-term solution involving a 3rd 115 kV import circuit.

Fulton-Lakeville-Geysers Long-Term Transmission Study

ISO will provide comments and recommendations on study alternatives.

Presentation and Discussion
Overview

Mark Esguerra provided an introduction to Stakeholder Meeting #3.  The focus of this meeting is to introduce the extended planning areas for the 2001 Expansion Plan.  The Extended Planning Assessments are planning studies with a timeframe of 8 years or longer.  They are intended to identify long-term solutions for a particular planning area.  The following Extended Planning Areas are introduced:

 Greater Bay Area (2002)

 San Jose Area

 Greater Fresno Long Term

 Yuba and Sutter Counties

 Humboldt Stability

 Fulton-Lakeville-Geysers

In addition to the areas listed above, there are several long-term studies where the process has been initiated.  The following long term planning studies already under way are:

 San Francisco-Peninsula Transmission

 Greater Bay Area

 SVP-PG&E Interconnection

 Path 15

 Sonoma-Napa

Mark Esguerra also provided an update to 29 transmission projects.  The expected in-service date for these projects ranged from 2001 to 2005.  Stakeholders requested additional information for these projects and this will be done offline or through email.

Bay Area 2002 Load Serving Capability Study

Marco Rios presented the results of the 2002 Bay Area Load Serving Capability Study.  The study was done on an expedited basis and a draft report was posted on March 16, 2001.  The study’s emphasis was to determine the maximum Bay Area load that can be served while maintaining adequate reactive margin, by simulating system conditions similar to June 14, 2000, when there were multiple generating unit outages.

The following are the results of the 2002 Bay Area Load Serving Capability Study:

 The Bay Area transmission system can support an electric load demand up to 10,750 MW in year 2002, while maintaining sufficient reactive margin levels.

 The Bay Area load serving capability further increases to 11,260 MW should the Delta Energy Center by operational before the summer of 2002.

 Due to thermal concerns to the Moss Landing-Metcalf 230 kV circuits, the Bay Area transmission system can support an electric load demand up to 10,350 MW.

 The Bay Area load serving capability further increases to 10,850 MW should the Delta Energy Center be operational before summer 2002.

 The projected Bay Area 2002 load is 9,700 MW.

Follow-up items include an additional study with the Bay Area Load Level at 9,943 MW and the Moss Landing Re-powering project and Delta Energy Center project not available. The study will also use the following Bay Area Generation Outage Criteria (Approximately 1,000 MW unavailable):

 Pittsburg Unit #7 off-line

 Potrero Unit #3 off-line

 1 San Francisco CT off-line

 1 Bay Area CT off-line

The schedule to finalize the study is April 11, 2001.

Comments on 2002 Bay Area Load Serving Capability Study

Barry Flynn addressed the need to keep the Bay Area generation consistent and the COI import level at a more conservative level.  Les Pereira addressed the need for PG&E to stay coordinated with Operations and ISO in developing the Under Voltage Relay Setting and load-shedding scheme at Newark for year 2002.

Bay Area Bulk Transmission Import Study Update

Eric Law presented an update to the Bay Area Bulk Transmission Import Study.  The objective of this study is to determine a project that meets the 2011 Bay Area loads.  Currently, the study is in the 2011 base case development stage.  The development of the 2011 base case requires stakeholder comments and will be posted on the ISO web site.

Comments on Bay Area Bulk Transmission Study

A suggestion was made to show the new Bay Area generation expected on line by 2011. Bay Area generation will be a planned sensitivity.  Generation units will be used to determine their effectiveness and the load levels that can be served.  Below is a table summarizing other Bay Area Generation that should be included as part of the study:

	Name
	PMAX
	CEC Status

	United Golden Gate
	570 MW
	In licensing

	Contra Costa Expansion
	590 MW
	In licensing

	Metcalf Energy Center
	600 MW
	In licensing

	Valero Co-Gen (Benecia)
	50 MW
	Not required

	Hayward (Russell City)
	600 MW
	

	Gilroy – peakers
	50-200 MW
	Mercury News

	Silicon Valley Power – peakers
	50-100 MW
	Mercury News

	US Dataport Co-Gen
	250 MW
	CEC meeting

	Sparta Energy (near SJ State)
	124 MW
	Mercury News

	Potrero 7
	530 MW
	In licensing


San Jose Long-Term Project

Kevin Kozminski presented the San Jose long-term project.  The objective of this project is to plan out transmission system improvements that will provide reliable service to the San Jose area for at least 10 years.  The existing transmission system in San Jose is primarily made up of a 115 kV network with the northern side supplied by Newark and the southern side supplied by Metcalf.  There is little in-area generation and the area pockets require a high level of reliability.  The San Jose area has a healthy load growth and increases with the addition of server farm loads.

The foreseen problems to the area transmission system are the following:

 115 kV network being “max’ed out”

 The 230/115 kV banks at Newark loaded up

 The 500/230 kV and 230/115 kV banks at Metcalf loaded up

 Low reactive margins

A possible solution to address the foreseen problems is to sectionalize the 115 kV network.  This involves breaking up the network system into smaller subsystems or “pockets” and providing back-ties for emergency service.  Back-ties are necessary because some subsystems will have a DCTL as their primary feed.

The tentative schedule to finalize the study is October 2001.

Comments on the San Jose Long-Term Project

Dan Wood of USE suggested an additional C.3 contingency involving the loss of parallel 500 kV lines into the bay area (Although, these lines are not on the same tower).  Another comment from the stakeholder group asks for verification that the back-ties for each subsystem be sized to 60-70% of its peak pocket load.  

Greater Fresno Long-Term Assessment

Monte Meredith presented the Greater Fresno Long-Terms Assessment.  The objective of this project is to plan out transmission system improvements that will provide reliable service to the Greater Fresno area for the long-term.  The Greater Fresno is located in the San Joaquin Valley and includes Merced, Madera, Fresno, and Kings counties.  The transmission network is made up of 230 kV, 115 kV and 70 kV systems.  Majority of the generation within the Greater Fresno area consists of hydro units with the largest being the Helms Pump Storage Plant.  

The foreseen problems to the area transmission system are the following:

 Existing resources may be inadequate to meet the 2006 forecast or beyond under contingency situations.

 The pumping window may be reduced due to load growth.

 Voltage stability may be in question due to low reactive margins at Wilson, Gregg, McCall, and Gates.

Several objectives of the Fresno study would be to reduce reliance on Hydro generation, increase the import/load serving capability into the Greater Fresno area, and ensure voltage stability.  The following study alternatives addresses these needs:

 Generation within Fresno

 Gates-Gregg 230 kV DCTL

 Raisin City Jct. 230 kV Switching Station

 Gates-Gregg 500 kV Line

 Raisin City Jct. 500 kV Switching Station

 Existing System Reinforcement

 Big Creek Interconnection

 Extra Source from Wilson Substation

The following are additional sensitivities to the Greater Fresno Long-Term Study:

 Sensitivities for peak conditions including low hydro and various Helms PGP output.

 Sensitivities for off-peak conditions including specific loading levels with 3, 2, and 1 pumping and various hydro generation.

 Sensitivities on the Path 15 flows.

The current schedule to finalize the study plan is April 20, 2001.

Comments on the Greater Fresno Long-Term Study

A comment from the stakeholder group suggested looking into any known environmental issues on the Gates-Gregg circuit alternative.  Stakeholders also suggested providing a list of proposed Fresno area generation projects.

Yuba and Sutter Counties Long-Term Transmission
Lorenzo Thompson presented the Yuba and Sutter Counties Long-Term Study.   The objective of this study is to plan out transmission system improvements that will provide reliable service to the Yuba and Sutter Counties for at least 10 years.  Yuba and Sutter Counties are located in Sierra division which serves are a major pathway between North Valley and Sacramento divisions.  The transmission system is made up of 60 kV and 115 kV networks.  Generation supporting the Yuba/Sutter area is Colgate Ph, Narrows Ph, and Yuba City Co-gen.

Some reliability issues to the area transmission system are the following:

 Future load growth will deplete the area’s electric capability.

 Sources to serve the area load centers cover long distances.

 The area’s transmission lines are low in capacity.

 There are numerous distribution substations involved in the system.

The following study alternatives address these reliability needs:

 Convert Palermo-Rio Oso 115 kV to 230 kV

 New 230/115 kV substation between Palermo and Rio Oso

 Convert Table Mountain-Pease 60 kV to 115 kV

 Re-conductor Colgate-Smartsville-East Nicolaus 60 kV lines

 Separate Palermo-Rio Oso 115 kV lines into North and South Loops

 Separate Colgate-Smartsville-Marysville-East Nicolaus-Pease 60 kV into a Sutter and Yuba system. 

The tentative schedule to finalize the study is September 2001.

Humboldt Stability Study

Mark Esguerra presented the Humboldt Stability Study. The objective of this study is to determine the maximum Humboldt load allowable under the existing system, the maximum fault clearing time allowable under the 2001 winter peak load, and ensure a reliable power supply to the Humboldt area.  The Humboldt area is located in the northwest corner of PG&E’s service territory.  The transmission system is comprised of 60 kV and 115 kV networks.

Some stability concerns to the Humboldt area are the following:

 The Cottonwood-Bridgeville 115 kV outage with a clearing time of around 35 cycles at Bridgeville.

 The clearing times of 60 kV line outages like the Humboldt Bay 60 kV breakers at 38 cycles.

 Potential 60 kV instability caused by a single 60 kV line outage or an overlapping generator and line outage.

The following study alternatives address these stability concerns:

 Cottonwood-Bridgeville 115 kV protection upgrades would decrease the clearing time to 8 cycles or better at Bridgeville.

 Decrease the clearing times at Humboldt Bay.

 Develop long-term transmission plans assuming the stability questions are answered.  ISO suggested a long-term solution involving a 3rd 115 kV import circuit.

The tentative schedule for a draft report is July 13, 2001.

Fulton-Lakeville-Geysers Long-Term Transmission Study

Chad Thomson presented the Fulton-Lakeville-Geysers Long-Term Transmission Study.  The objective of this study is to provide reliable power to the Fulton-Lakeville-Geysers area for the long term.  The Fulton-Lakeville-Geysers area is made up of Napa, Sonoma, Mendocino, and Lake counties.  The main sources into the area are 230 kV ties from Vaca-Dixon, Ignacio, and Sobrante, two 115 kV circuits from Cortina, and local generation made up primarily by geothermal plants.

Some reliability issues to the area transmission system are the following:

 Reduction in availability of local sources specifically geysers stream.

 Electric demand continues to increase at a load growth of 20 to 40 MW/year.

The following study alternatives address these reliability issues:

 New 230 kV transmission circuits into the area such as a double circuit from Vaca-Dixon to Fulton or a double circuit from Cortina to Mendocino.

 Reinforce 115 kV transmission system

Attachment 1:  Email dated April 9, 2001from Les Pereira of NCPA to PG&E, ISO and Stakeholders

-----Original Message-----

From: Les Pereira [mailto:Les@ncpa.com]

Sent: Monday, April 09, 2001 12:03 PM

Subject: RE: PG&E Meeting #3 Minutes

Sensitivity: Confidential

Mark:

You have not included my written comments on the Bay Area Study, nor the

discussion PG&E, CAISO and I had on those comments. All you have is an

action item for undervoltage relay shedding.  Also you have not included me

in the list of persons attending the meeting - (for the third time).  

My comments on the Final Bay Area study report were that the study results

raises basic questions. On June 14, 2000, load shedding occurred when the

system voltages reached about 227 kV at Newark, the "voltage collapse "

point stated in the Executive Summary. However, the Operating Points in all

of the Attachments A to H show Newark voltage levels in the range of 213 kV

to 222 kV for the Newark Voltage-MVAR curves.  These are very low voltages

to start with - immediately after the contingency - let alone proceeding

downhill towards the even lower collapse voltages of about 205 to 210 kV. At

what levels are the undervoltage load shedding relays set at - to

automatically shed customer loads?  The load level of 10750 MW that is

recommended is optimistic - unless CAISO/PG&E plans to operate the system at

voltage levels of 93% for the stated conditions. Hence some load shedding

should be expected at this point.

Furthermore, for 3 meetings now - going back to Jan. 22, 01, I have

requested the details of PG&E's project T745 - Bay Area Reactive Support

with an EDRO of June 2002 which has a Static VAR Compensator named as the

solution.  It is clear that this will not make it by June 2002, and appears

it has not yet been studied.  The study schedule and status should be given.

Please include my written comments and verbal discussion at the meeting as

part of the Minutes of the meeting. Your comments in reply and the ISO's may

also be included.

There does not seem to be much point to publishing minutes if recording of

key points of discussion is not done.

Les Pereira

-----Original Message-----

From: Esguerra, P Mark [mailto:PME8@pge.com]

Sent: Monday, April 09, 2001 10:56 AM

Subject: PG&E Meeting #3 Minutes

Importance: High

Sensitivity: Personal

Stakeholders,

The stakeholder meeting #3 minutes are attached.  These minutes will also be

posted on the Cal-ISO web-site.

Regards,

Mark Esguerra

PG&E-Transmission Planning

415-973-4380

Attachment 2:  PG&E Response to Email dated April 9, 2001 from Les Pereira of NCPA

Response to Les Pereira Comments

The Bay Area 2002 Load Serving Capability Study was an expedited study intended to determine the Bay Area load serving capability for the year 2002, as well as identify any needed transmission projects that would increase the capability to serve load for year 2002.  The study emphasis was to determine the Bay Area load serving capability while still protecting against specific contingency conditions and maintaining sufficient reactive margin levels (positive margin).

The California ISO determined the minimum operating voltage level allowed for Newark substation on June 14, 2000 to be 227 kV.  Given the system conditions on June 14, 2000, it was determined that a stage 3 (Bay Area firm load) would be called to protect the Bay Area system from the next worst contingency which could have led to a voltage collapse situation for the Bay Area.

According to the study results, the planned 2001 and 2002 Bay Area projects provide increased reactive support for the Greater Bay Area, which may allow us to lower the undervoltage load shed relay settings at Newark
.  The 2001 and 2002 projects that provide increased reactive support for the Greater Bay Area are the following:

Transmission Projects

· Tesla-Newark 230 kV Line

· Ravenswood 230 kV Loop

· Tesla 500/230 kV Transformer

· Metcalf 500 kV 350 MVAr Shunt Capacitors

· Metcalf-Monta Vista 230 kV Line Separation

· Martin 115 kV Shunt Capacitors (200 MVAr total)

· Hunters Point Units #2 and #3 Conversion to Synchronous Condensers

· Tracy 500/230 kV Bank

Generation Projects

· Los Medanos Energy Center

· Delta Energy Center

· Duke – Moss Landing Re-powering Project

The study results show that under a scenario with multiple units off-line under emergency conditions for summer 2002, the reactive margin at Newark is between 121 and 461 MVAr.  The post contingency voltage levels vary between 213 kV and 221 kV.  

The undervoltage load shedding settings will not affect operation of the system because the intention is to set them such that no single contingency would result in voltage collapse.  Thus, the settings will never be anywhere near the operating voltages.

Project T745:  Bay Area Reactive Margin Project

Currently, PG&E has contracted the studies for this project to GE.  GE’s preliminary results show that SVC devices will not be required for year 2002.  The final results for this project will be provided before the next PG&E stakeholders meeting.

�  In the QV analysis provided, the voltage collapse points or nose points ranged from 200 kV to 212 kV.  This information suggests that, for the outages ran, the Newark and San Mateo UVLS relay voltage trip level could be lowered.





15

