[image: image1.wmf]
TECHNICAL AND OPERATIONAL

DUE DILIGENCE REPORT

OF

PROJECT BATTLESHIP

Prepared for Enron North America

July 2, 2001

CONFIDENTIAL

FORWARD

This report was prepared by Enron North America Power Technical Analysis, EEOS Global Asset Management, and Enron Corporate Environmental under the direction and in support of Enron North America (ENA) East Origination.  Information contained herein is a culmination of effort from the ENA/Project Dodger due diligence team. 

During April and early May, 2001 the ENA/Project Dodger due diligence team toured the Edison Mission Corporation’s Brooklyn Navy Yard Power Plant.  The purpose of the site visits was to provide a technical review of the facilities, query the plant staff on operations, engineering and environmental concerns, and assess overall plant conditions that would support the decision making process on the potential ownership acquisition of this facility by ENA. 

Key areas reviewed included plant material condition and equipment maintenance concerns, understanding of O&M practices and performance assumptions, future capital expenditure requirements to maintain reliability, evaluation of potential equipment and plant upgrades, onsite hazards and liabilities, and operating restrictions. Issues not reviewed included: 

· Fuel Contracts

· Legal 

· Tax & Insurance Issues

The Due Diligence team members were:

· Karl Masani, Enron Global Asset Operations Manager - O&M Review and Physical Plant Assessment

· Dan Williams, Director, Power Technical Analysis – Due Diligence Coordination, Operations And Physical Plant Assessment

· Bill Curra, Environmental Engineer, Enron Corp.Environmental – Environmental Engineering Review

· David Marks – Director, ENA East Origination

· Bill Keeney, Manager – ENA Transactions Structuring (not present on plant tour)

Contacted personnel at the plant were:

· Michael Brown, Plant Manager – Brooklyn Navy Yard

· Maria Rigatti, Asset Manager – Edison Mission

Overall assessment of the plants was favorable towards acquisition of the offered equity position.  No physical plant issues representing a risk to the future operation and maintenance of these facilities that would constitute other than normal wear and replacement under corrective or preventive maintenance standard industry practice were found to exist except for the history of excessive tube leaks in the heat recovery boilers.

See the summary of risk issues included in Section VI of this report.

TABLE OF CONTENTS

PAGE

I.
EXECUTIVE SUMMARY







     4

II. PLANT DEMOGRAPHICS






     5 

III. PHYSICAL PLANT ASSESSMENT





     6

IV. OPERATIONS & MAINTENANCE                                                                           6

V. EXPANSION & UPGRADE                                                                                        10

VI. SUMMARY




                                                                 10

· ATTACHMENT A 








     14

FACILITY OVERVIEW OF BROOKLYN NAVY YARD COGEN

· ATTACHMENT B 








     22

OWNERSHIP STRUCTURE 

· ATTACHMENT C








     23

POWER PLANT’S O&M ORGANIZATION AND COST ANALYSIS

· ATTACHMENT D








     49

MAJOR MAINTANENCE HISTORY TIMELINE

· ATTACHMENT E








     51

ENVIRONMENTAL DUE DILIGENCE .

· ATTACHMENT F








     68

DIRECTIONS TO BROOKLYN NAVY YARD COGEN PLANT

· ATTACHMENT G








     70
PERFORMANCE DATA

I. EXECUTIVE SUMMARY

Brooklyn Navy Yard

BNY is located on a 6.8-acre site in the Brooklyn Navy Yard in Brooklyn, New York.  The Brooklyn Navy Yard is an industrial park operated by a local development corporation, the Brooklyn Navy Yard Development Corporation (“BNYDC”), under a 99-year lease with the City of New York.  The site is at the edge of a ship basin off the East River and is leased from BNYDC by Brooklyn Navy Yard Cogeneration Partners (“BNYCP”), BNY’s owner.  B-41 Associates, L.P. (“B-41”), an indirect affiliate of York Research, and Mission Energy New York, Inc. (“MENY”), a subsidiary of Edison Mission Energy (“EME”), each have 50% ownership interest in BNYCP.

BNY consists of two combined cycle/cogeneration trains and associated electrical, control, water, and civil works.  Each train includes a Siemens Power Corporation (“SPC”) V84.2 combustion turbine and generator set, an Asea Brown Boveri/Combustion Engineering heat recovery steam generator (“HRSG”), and an SPC steam turbine and generator set.  This equipment and the majority of the other Project equipment are located in a pre-existing structure, Building 41, which formerly housed a coal fired power plant.

BNY was designed and constructed by PMNC, a joint venture led by Parsons Main of New York, Inc. (“Parsons Main”) which included Nab Construction Corporation and L.K. Cornstock Company, Inc.  BNY began operating on November 1, 1996.  BNY is contractually obligated to provide 220 MW of electric power and steam ranging from 550,000 lbs/hr in the summer to up to 800,000 lbs/hr (or more in certain conditions) in the winter over 40 years to Consolidated Edison Company of New York (“Con Ed”) under an energy sales agreement (the “Con Ed ESA”) through October 31, 2036.  There is considerable flexibility in the Project to vary the outputs of steam and power as directed by Con Ed.  Con Ed can reduce the quantity of steam purchased after the twentieth year if Con Ed’s peak steam load falls below 10.0 million lbs/hr.  The Project was also designed to provide steam and power to BNYDC under an energy sales agreement (the “BNYDC ESA”), the steam to the Red Hook Wastewater Treatment Plant (“Red Hook”).

Natural gas supply for the Project is supplied by two Canadian producers and one American producer, is managed by Long Island Lighting Company (“LILCO”), and is locally transported on an interruptible basis by Brooklyn Union Gas Company (“BUG”).  Distillate fuel oil is utilized as a backup fuel during any gas interruption of up to nineteen days in the winter periods.

BNY is a Qualifying Facility (“QF”) under the Public Utility Regulatory Policies Act of 1978 (“PURPA”) as a cogenerator, and was determined to be an Exempt Wholesale Generator (“EWG”) under the Energy Policy Act of 1992.

The Facility is located at 63 Flushing Avenue, Brooklyn, New York, within the former Brooklyn Navy Yard on approximately 6.8 acres of leased property.  The primary cogeneration facility is located in a brick building identified as Building 41 and includes two parallel independent combined cycle cogeneration trains and associated auxillaries and control systems.  The Facility is under contract to Consolidated Edison (Con Ed) to provide 220 megawatts of electric power and 550,000 pounds of steam per hour in the summer and 800,000 pounds of steam per hour in the winter.  The Facility also provides electricity and steam under contract to BNYDC for use within the industrial park and supplies steam to the City of New York Red Hook Wastewater Treatment Plant.  The Facility is primarily fueled with interruptible natural gas.  Low sulfur diesel fuel is permitted for use in each train for up to 19 days per year.

All required permits and licenses, which are essential for operation of the Project, have been maintained, the status of which are detailed in Attachment E.

In general, it is our opinion that the Project is designed in accordance with good engineering practice and that with the continued proper operation and maintenance expected from the O&M contractors, it is capable of providing net operating income necessary to service lease costs, debt service, rent payments, and provide a reasonable profit.

II. PLANTS DEMOGRAPHICS

PRINCIPAL PARTIES:

Project Operators:  Brooklyn Navy Yard Cogeneration Partners, L.P. a partnership of Edison Mission and York Research

Design/Construction:  Parsons Main of New York in a Joint Venture with Nabb Construction Company and L.K. Comstock Company, Inc.

Plant Operator:  Palmark, Inc. a subsidiary of Primesouth, Inc.

Fuel Operator:  Brooklyn Union Gas is LDC, Long Island Lighting Company (LILCO) is the fuel manager.

Power Purchaser:  Consolidated Edison

Steam Hosts:  Consolidated Edison, Brooklyn Navy Yard Development Corporation, and Red Hook Wastewater Treatment Plant.

PROJECT CHARACTERISTICS:

· Two power blocks of 1x1 combined cycle delivering steam to multiple host facilities

· Commercial operation date was November 1, 1996

· 286 Mw nominal plant rating

· Excessive boiler tube leaks should be alleviated by new boiler water treatment plant

· Gas turbines should be run above 70% load for stable operation

PROJECT BENEFITS:

· Project is well sited for delivery of power into New York City area.

· Plant can be upgraded to higher capacity merchant plant.

· Selling into the power market above the current plant’s capacity.

· There is considerable flexibility in the Project to vary the outputs of steam and power as directed by Con Ed.  

III. PHYSICAL PLANT ASSESSMENT

1. STEAM TURBINES/GENERATORS 

Included in Section IV following.

2. GAS TURBINE/GENERATORS 

See Attachment G 

3. HEAT RECOVERY STEAM GENERATORS

See Section IV following.

4. COOLING TOWER  OR CIRCULATING WATER SYSTEM & MAIN CONDENSER

See major equipment list.

5. AUXILIARY BOILERS

A 200 kpph rated boiler is available on-site.

6. TRANSFORMERS AND ELECTRICAL 

No data.

7. ENVIRONMENTAL

See Attachment E.

8. OTHER

Other plant equipment is assessed in Section IV following.

IV
OPERATIONS & MAINTENANCE

Brooklyn Navy Yard technical due diligence – June 2, 2000

Jeff Hoover, Bill Keeney, Stephanie Grimm (Babcock and Wilcox field service engineer) and  Wayne Mays met with Chris Trebold and Michael Brown at the Brooklyn Navy Yard generation station.

Art Stappenbech from East Coast Power, Len Gunderson from ENA and Wayne Mays had completed a technical due diligence review on the Brooklyn Navy Yard in January.  Purpose of this followup visit was primarily to:

(1) Address our concerns about the HRSG tube leak problems and the steps they have taken to follow up on this problem.

(2) Review the changes they have made to the major maintenance program over the next couple of years.

(3) Confirm the thermal efficiency and output degradation numbers provided by previously.

(4) Understand the performance versus O&M budget over the first four months of 2000.

(5) Look at the possibility of plant expansion.

(6) Discuss recent ConEd plant curtailments.

HRSG tube leaks

For a new plant, there have been a surprising number of tube leaks.  In March 1999, a tube leak occurred in unit 1 lower header.  The tube was plugged and the HRSG returned to service.  At the first major maintenance on combustion turbine #2 in April 1999, an inspection of the HRSG was conducted by ABB.  ABB determined that there was evidence of erosion/corrosion which would not be expected to occur in such a new plant.  This damage seemed to be isolated to the area close to the economizer header – further away from the header the tubing looked good.

ABB attributed some of the damage to poor water chemistry (pH was causing 100 times the normal corrosive effects inside the tubes). A contributing factor is the tube material.  Subsequently, about 300 tubes were cut off and the ends connected to the economizer header replaced with a higher grade of material (chrome moly changed out with T-22).  This was a difficult and expensive process and there has been widespread speculation at the plant about whether they have done everything they can to address the problem.  The plant manager believes a contributing factor is the flow turbulence caused by poor design and construction at the header.

The plant had some concerns about this study being done by ABB because they provided the HRSG.  A second opinion was obtained from Deltak, which agreed with the findings of the ABB team.

Over a four-week period in December 1999 and January 2000, there were over 100 hours of forced outage caused by tube leaks in the HRSG.  This heightened the level of concern.  Since then, the partnership has gone through mediation and is now suing the company that provided the HRSG to ABB (PMNC – Parsons Main Nabb Construction LM Comstock). We suspect that the lawsuit won’t go well because of the obvious poor plant chemistry. The poor water chemistry can be attributed to the IWT water treatment plant being commissioned so many months after commercial operation of the power plant and the fact that plant operating personnel may not have payed enough attention to boiler water chemistry early on.

For the future, the partnership is taking a “wait and see” approach with no present plans to do more tube replacements.  We discussed this approach internally and agreed that this is most appropriate course of action.  Taking a major outage to do a large tube replacement would reduce plant availability below what is expected will be a decreasing number of tube leak forced outages.

BNY is currently considering re-tubing 60% of both boilers at a cost of up to $6 million each if operational reliability is affected in the future.

Major maintenance program changes

From our previous visit we noted a change in the major maintenance program.  Instead of major maintenance on CT #1 and CT #2 occurring in 2002, they have now maintenance on CT #2 to Fall 2001 while leaving CT #1 in Fall 2002.  The reason that the plant manager gave us was that the equivalent operating hours target for maintenance is being moved from 25,000 towards 35,000 although if this were true the CT #2 outage would still occur in 2002.  We think the real reason was given by Chris Trebold when he told our us that they need to spread the outages to different years to prevent a debt coverage problem.  There is a small difference in outage scope and cost, but no change in outage durations from previous discussions.

Confirm the thermal efficiency and output degradation numbers previously provided.

From our experience with GE frame machines we expect thermal efficiency and output degradation numbers to be in the range of 5 percent and 2.5 percent respectively.  The 1.5 percent figures supplied by the plant didn’t seem correct.  The information provided by Seimens and which we now have a copy of seems to confirm the plant’s assumptions.

Actual performance versus expected performance.

Expected plant heatrates without degradation are in the range of  8,241 – 11,105 Btu/Kwh (HHV), as shown in Attachment G. The actual net plant heatrate reported for April, 2000 was 10,441.9 Btu/Kwh on average. Average capacity was 231.6 Mw during this month. The values for actual plant performance compare favorably with expected values. Obviously, plant performance is highly dependent upon how the plant is to be dispatched.

Possibility of plant expansion.

There is an approximate two-acre parcel of land next to the new water treatment plant, which the plant had under lease through May 31, 2001.  The site appears large enough to accommodate another small generating unit such as a LM6000.  It may also support the additional 600 kpph of auxiliary boilers needed to make the existing combined cycle units fully merchant power units. This land undoubtedly has value either for sale as a developable site or to actually locate another unit.

Of greater interest was the possibility of inlet air cooling at the existing plant.  The performance and costs for two types of inlet air cooling systems are evaluated in the next section.  Selling into the market above 220 MW needs to be evaluated as another benefit of our acquisition of Edison Mission’s share of this partnership.

Inlet Chilling of Gas Turbines

Combustion turbine output is proportional to the air mass flow rate. At higher ambient temperatures the turbines lose capacity since the mass flow rate of air decreases as the air becomes less dense. This degradation of output at high ambient temperatures can be compensated by cooling the air to the compressor section. In addition to increased to increased output from the combustion turbine operating at lower ambient temperatures, there is an increase in Heat Recovery Steam Generator (HRSG) output that can enhance either steam sales or electric output from the steam turbines. The increase in output through cooling of the inlet air can be achieved without additional environmental permits.

There are two basic methods of inlet cooling: evaporative cooling and refrigeration cooling. With evaporative cooling, water in the form of a fine mist/fog is brought into contact with the incoming air to the gas turbine. The water evaporates as it absorbs heat from the incoming air thereby reducing the dry bulb temperature. These systems work well in relatively dry climates since they can cool the air to near the wet bulb temperature. In areas of higher humidity they are less effective, but can still achieve some cooling. Refrigeration cooling or “chilling” utilizes a cooling medium (such as treated water) in a coil arrangement to cool the incoming air to below the wet bulb temperature. This chilling is accomplished through mechanical means such as electric or steam driven motors/compressors or an absorption process (such as lithium bromide). Through the use of a chiller ssystem inlet air temperatures can be lowered to the 45-50 degF range.

The following factors should be considered when deciding whether or not an inlet cooling system is cost effective for installation, and if so, which type to install:

· Ambient temperatures and relative humidity of the site

· Slope of the turbine performance curve (output vs. inlet temperature)

· Hours of operation at ambient conditions

· Sales price for the additional output

· Space considerations for the new equipment

· Capital cost and operating costs for the new system.

Because of the higher humidities in Brooklyn, we have made a brief evaluation of the impact of an inlet chiller application to overall plant performance. We applied a mechanical chiller, knowing that they are more efficient than a typical absorption chiller and the mechanical chiller would allow more steam available for power generation. This mechanical compression refrigeration system’s cooling cycle begins at the expansion valve of the evaporator where liquid refrigerant expands to a lower pressure, starts to boil and picks up heat from the surrounding area. Refrigerant vapor leaving the evaporator is compressed to raise its temperature higher than that of the available cooling water supply. High-pressure high-temperature gas leaves the compressor to pass through the condenser. Here lower temperature cooling water removes heat picked up by the refrigerant in the evaporator, piping and compressor. The refrgerant then condenses to liquid. In an indirect system of this type, the evaporator cools the water that in turn does the actual cooling through a cooling coil in the gas turbine inlet air duct.

In this analysis we selected a 1925-ton single-stage mechanical chiller for each gas turbine. This size system could reduce the inlet air temperature to the gas turbine by 31 degF. Refrigerating capacity is measurred in tons. One ton of refrigeration means heat removal at the rate of 200 Btu per minute, 12,000 Btu per hour or 288,000 Btu per 24 hours.

In the expected performance shown in Attachment G for the 90 degF, 50% relative humidity case with 200 kpph of steam sales, we would expect a capacity of about 251,905 Kw with a heatrate of 7669 Btu/Kwh (LHV) or 8510 Btu/Kwh (HHV). With an 85% effective evaporative cooler applied to each gas turbine at these same conditions, one would expect a plant capacity of about 263,947 Kw with a heatrate of 7576 Btu/Kwh (LHV) or 8406 Btu/Kwh (HHV). Applying the 1925-ton chiller to each gas turbine described above at these same conditions, the expected plant capacity would be about 270,776 Kw at a heatrate of 7718 Btu/Kwh (LHV) or 8564 Btu/Kwh (HHV). The 19 Megawatts of additional capacity at 90 degF with only a slight increase in plant net heatrate should be commercially evaluated. To select the optimized cooling system for this application, the Owners may wish authorize a more detailed engineering study.

Curtailments

For a year, ConEd plant curtailments were below budget but March, 2000 was a particularly bad month due to several unusual operating factors on the ConEd system.  

Operation Assessment

Staffing Level

Staffing level seems adequate to operate a facility of this type. A complete organization chart is included in this report.  The maintenance crew handles all preventive and corrective maintenance functions, with specialized maintenance.

Staffing Qualifications

The operations crew goes through qualification training before they are able to operate in the control room. All operators are equally qualified and rotate between the field and the control room.

Operations

All PMs and corrective maintenance is done on off-peak, zero export times.  If the plant does experience a forced outage, a schedule of corrective maintenance tasks is done during the down time.  For the year 2000, the plants capacity factor was projected to be 83.9% based on a nominal rating of 286 Mw.

Maintenance

Reviewing the work order reports prior to the upgrade reveals a healthy split between emergency/breakdown work orders and preventive maintenance work orders.  By all indications, it appears that the preventive maintenance done on the plant is providing for plant stability.

Safety

The facility has a safety record of just a few days running without a lost time injury. There is very little access around equipment in the water treatment building, which could be interpreted as an OSHA violation for personnel access representing a risk to the Owners. Another potential OSHA violation is personnel noise exposure in the small plant maintenance area.  

V. EXPANSION & UPGRADE

There are no significant plant expansions or upgrades planned.

VI. SUMMARY

As a result of this technical due diligence investigation, the ENA due diligence team finds no fatal flaws in the Brooklyn Navy Yard generating facilities. The plant appears to be fairly well operated and maintained by Primesouth and Palmark.

Brooklyn Navy Yard

1. The BNY design, construction, and technology appears technically sound and suitable for providing base load power and steam generation pursuant to the requirements of the Project Agreements.  There is considerable flexibility to vary the outputs of steam and power.  The Project site is suitable for a gas-fired combined cycle/cogeneration power plant.  Major equipment embodies proven technology and was supplied by reputable manufacturers.  While earlier versions of the V84.2 combustion turbine experienced reliability shortfalls, SPC had indicated that all of the resulting design corrections and enhancements developed by SPC have been incorporated into the Project’s V84.2 units.

2. The construction of BNY was completed and BNY became operational in November 1996.  Stone & Webster understands that BNYCP is currently involved in litigation with PMNC over performance of the construction contract but believes that the issues involved in the current litigation do not materially affect the performance of the Project.  Stone & Webster was informed that EME has provided an indemnity to BNYCP for this risk.  BNYCP has engaged contractors who have substantially completed the contract work and punchlist items not finished by PMNC.  BNYCP is replacing the existing trailer-mounted water treatment system (i.e., third party contract to Ecolochem) by constructing a permanent on-site system at an estimated total cost of $15.6 million expected to be completed by February 1999.  The costs associated with the purchase and installation of this system are covered  by a fund established for such purpose from the proceeds of the December 1997 bond offering.  BNYCP also incorporated Project improvements, including improving the gas compressor discharge bypass to further improve plant heat rate.

3. BNY performance to date, combined with the seasonal testing required under the Con Ed ESA and the performance test conducted by Black & Veatch, confirms that BNY has produced the electrical and steam capacity contemplated under the Con Ed ESA in all seasonal periods.  In 1997, the Project has achieved a cumulative equivalent availability (“EA”) under the Con Ed ESA of 91.10% as reported by the Project Operator and has improved to 98.4% for the first quarter of 1998.  A 93.0% EA for all hours is required to receive the full Con Ed electric and steam capacity payments.

4. BNY has achieved QF thermal and efficiency standards to date.  Stone & Webster expects the Project to continue to be able to meet the QF standards for the term of the Con Ed ESA, although a QF status is not required for the Con Ed ESA.  BNY is an EWG and can physically sell electric power above 220 MW to Con Ed or to other purchasers through the Con Ed transmission system if BNY cannot sell the current projected quantities of steam after the twentieth year.

5. Stone & Webster expected BNY to achieve a long term all-hour average EA of 90.6% provided that Palmark operates and maintains the Project in accordance with the O&M Agreement and within accepted industry practice, and the BNYCP completes the work items not performed by PMNC, and implements Project improvements as mentioned previously.  Nothing about the operating history to date is inconsistent with its expected performance.  Actual operating reports for the year 1999 show that BNY has been able to maintain annual Equivalent Availabilities of better than 93% and the Winter EA of 95% as required by their contractual obligations as reported by Palmark. This has happened even in the face of all the boiler tube leak outages that occurred in 1999. Palmark appears capable and qualified to operate and maintain BNY in accordance with the O&M Agreement and within accepted industry standards, and has in place a preventive safety and maintenance program that should help ensure that BNY achieves the highest possible EA.  The basis for Palmark’s estimate of the costs of operating and maintaining BNY, including provision for major maintenance, is reasonable and in accordance with standard industry practice.

6. The Project Agreements, including the Con Ed ESA, the BNYDC ESA, the gas supply, transportation and management agreements, and the O&M Agreement, are technically reasonable and should allow BNY to achieve the results in the Financial Projections.  Steam containment specifications in the Con Ed ESA limit the use of chemical additives normally used to control corrosion in the HRSGs.  BNYCP currently meets the Con Ed steam specification.  The costs of replacing the HRSG tubes earlier than normal are included in the Financial Projections.

7. The Project was designed and equipped to comply with the air and water discharge permit limitations, including pollution control equipment to mitigate emissions of Nox and CO.

8. BNYCP has secured all major permits to operate BNY.  BNY is expected to continue operating under the existing air Permit to Operate and has applied for an air operating permit under Title V of the Clean Air Act Amendment (“CAAA”).  BNY has had infrequent air emission exceedances due to gas pressure fluctuations, but no notices of violation have been issued.

9. We expect BNY will have a useful physical operating life through the remaining 40 year term of the Con Ed ESA provided BNY is operated and maintained in accordance with the O&M Agreement and within accepted industry practice, and equipment (including combustion turbine rotor components, HRSG tubing, and control systems) are replaced on a timely basis as needed.


Technical, operational and maintenance risk issues are as follows:

(1) Water treatment plant – the US Filter provided plant is only now going through plant acceptance tests.  US Filter must have taken a terrible beating on this project because they were supposed to have had the plant in service over a year ago.  The shift assistant equipment operator will have the water treatment plant as a key area of responsibility.

(2) Staffing reductions – We don’t see opportunities for staff reductions even though they are very heavy for a plant of this size.  The relationship between the plant operating company, the unions and the plant location would prevent us from achieving a head count reduction.  The one area where there may be opportunities would be reduction of overtime but this dosen’t amount too much.

(3) They anticipate that the operating budget will continue to escalate at about 3.5 percent per year.  The operations contract locks this in through 2001 but after that the assumption is probably still valid.

(4) Mark Litterman had done some analysis on plant availability and determined that it was probably in the range of 90 to 92 percent.  Recent projections from the plant show they are looking at better than 92 percent as their projected availability.  We should use this in our assumptions.

(5) BNY has had major tube leaks in both boilers due boiler tube materials and design.  BNY is considering re-tubing 60% of both boilers at a cost of up to $6 million each if the tube leak problems persist.

(6) There is an unresolved corrective action directive mandated by the New York State Department of Environmental Conservation in connection with an accidental fuel release in April 1997.  A response action addressing the directive, relating to above ground storage tank integrity testing, has been implemented by the Facility; however there has been no concurrence from the agency signaling closure of the case.  This issue is discussed in Section 4.6 of Attachment E.

(7) The Facility Title V Air Permit mandates the use of 0.04% sulfur fuel.  According to the Facility EHS Manager, the availability of this grade of fuel may become limited in the future.  Options to address this include filing for a permit modification to relax the restriction on sulfur content, and/or switching to kerosene as a distillate fuel as discussed in Section 4.7 of Attachment E.

(8) The property lease agreement between the current lessor, Brooklyn Navy Yard Development Corporation, and the current lessee, Brooklyn Navy Yard Cogeneration Partners, L.P. was not available for review as of the date of this report.  It was unclear whether Enron will assume the existing lease agreement, or initiate a new agreement.  In either case, the contractual issue of “site restoration” should be given due consideration as discussed in Section 4.11 of attachment E.
Potential future capital costs are as follows :

· BNY has had major tube leaks in both boilers due boiler materials and design.  BNY is considering re-tubing 60% of both boilers at a cost of $6 million each. This may be considered a capital expenditure if deemed necessary.
· Inlet chiller systems to enhance gas turbine output may cost a total of $3.8 to $4 million.
· $4 million may be required to install 600 kpph of auxiliary boilers to allow combined cycle plant to be fully merchant.
ATTACHMENT

A

FACILITIES OVERVIEW 

BROOKLYN NAVY YARD

Project Design and Description

General Description:

BNY is a combined cycle/cogeneration power plant nominally rated at 286 MW at ISO conditions when producing electric power only.  The Project is comprised to the following main power generation components: (i) two SPC (Sieman Power Corporation} V84.2 combustion turbine and generator sets with dry low Nox (“DNL”) dual fuel combustors, each nominally rated at 103 MW, (ii) two Asea Brown Boveri/Combustion Engineering unfired, natural circulation 3-pressure level HRSGs with integral deaerators, and (iii) two SPC controlled extraction, admission, condensing, steam turbine and generator sets each nominally rated at 40 MW and a permanent water treatment system which will be operable in February 1999.  In normal operation, gas is burned in the combustion turbines to generate electric power.  The exhaust gases of each combustion turbine are converted in to steam in each of the two HRSGs.  The steam is then utilized by the steam turbine generators to produce additional power, or is exported to BNY’s steam hosts.

Location and Site Conditions:

BNY is located on a 6.8 acre site in the Brooklyn Navy Yard in Brooklyn, New York.  The site is at the edge of a ship basin off the East River and is leased from the BNYDC.  The Project is located in an existing building, B-41, of the Brooklyn Navy Yard.  The Brooklyn Navy Yard is a 261 acre facility, containing 4.3 million square feet of building space, located on the Brooklyn shoreline between the Manhattan and Williamsburg bridges.

Combustion Turbines:

The plant is equipped with two SPC V84.2 combustion turbine and generator sets.  The V84.2 is a heavy duty 60 hertz industrial machine with a nominal rating of 103 MW.  The V84.2 design is a scaled-down version of the V94, 50 hertz machine.  As of the date of this report, there are approximately 40 V84.2’s in operation, 23 in the United States and 17 abroad.  The V84.2 has a 17 stage compressor that produces a compression ratio of 11:1, two silo type combustors with gas and oil burners, and a four-stage turbine with a nominal inlet temperature of 2,020ºF.  The totally enclosed water to air cooled (“TEWAC”) generator is connected to the compressor end of the rotor and the exhaust exists axially from the turbine end.  Each combustion turbine generator is provided with an electronic turbine control system, combined vibration monitoring system, combined lube and control oil system, generator static excitation system, and generator static starting system.

Mechanical Systems:

Heat Recovery Steam Generators

The exhaust of each combustion turbine is ducted to an HRSG provided by Asea Brown Boveri/Combustion Engineering.  From this 1,000ºF exhaust gas, the HRSG produces steam at three pressure levels, 936 pounds per square inch gauge (“psig”), 121 psig, and 25 psig.  The high pressure (“HP”) steam is used to generate electricity in the steam turbine, for combustion turbine steam injection, and to supply export steam.  The intermediate pressure (“IP”) steam is supplied to the steam turbine to produce additional electricity and to supply export steam.  The low pressure steam (“LP”) is used in the integral deaerator to pre-heat and deoxygenate the HRSG feedwater.

Steam Turbines

SPC supplied two steam turbine and generator sets for the Project.  Each has a rating of 10 MW with full extraction and 40 MW without extraction.  To provide flexibility for export steam operations, each steam turbine is provided with intermediate extraction and admission ports in addition to the normal main steam inlet and condenser exhaust connections.  In normal operation, main steam is provided from the high pressure section of the HRSG, extraction steam is exported for sale, and admission steam is provided from the intermediate pressure section of the HRSG.  Each steam turbine generator is provided with an electro hydraulic turbine control system, combined vibration monitoring system, combined lube oil system with coolers and purifier, generator cooling system, and generator static excitation system.

Condensate and Feedwater System

The condensate and feedwater systems are auxiliary systems supporting the HRSG.  Condensate is collected in the hotwell of the condenser and pumped by either of two 100% capacity pumps to the suction side of the feedwater pumps.  Either one of two 100% capacity feedwater pumps delivers feedwater to the HRSG.

Emission Control Equipment:

Combustion Turbines

The gas burners are the SPC hybrid pre mix design that can produce low Nox  levels (9 ppm is guaranteed) without steam or water injection when burning gas.  The gas burners operate in pre mix mode at power levels above 70%.  The oil burners are a normal diffusion design and require water injection to limit Nox  to 42 ppm when burning oil.  In other V84.2 power plants which were cycled below full load, the pre mix burners were not fully reliable.  Base loaded V84.2s, however, such as the Project’s, are running successfully in pre mix mode.  SPC has had problems with V84.2 units switching between gas and oil firing because power must be reduced to about 70% for fuel switching which can affect the reliability of the fuel switching valves in the fuel oil system.  However, the BNY machines are not expected to have to switch fuels often due to the Project’s limited operation on fuel oil.  Therefore, fuel switching is not expected to have a significant impact on Project performance.

Catalyst Systems

Separate catalyst systems are provided in each HRSG to control the emissions of Nox   and CO.  Each catalyst bed is designed for full load exhaust gas flow and is located in its associated HRSG module to assure proper operating temperature.  Provisions are made for periodic replacement of the catalyst beds as dictated by catalyst performance.  In the SCR, aqueous ammonia is injected into the exhaust gas stream in vapor form, ahead of the catalyst, through a grid system that is designed to assure even distribution.  The Nox  to nitrogen and water with the use of an ammonia reagent.  The SCR system is designed to provide a stack outlet Nox  concentration of less than 3.5 ppm with an inlet concentration of no greater than 9 ppm and an ammonia slip of less than 10 ppm when firing gas.  When firing oil, the SCR is capable of reducing the 42 ppm in the exhaust gas to less than 10 ppm.  In order to reduce the exhaust CO concentration to permit limits and to prevent fouling of the downstream heat transfer surfaces, the Project also includes a CO catalyst which directly oxides CO to CO2  without the need for any chemical reagents.

CEMS System

The Continuous Emissions Monitoring System (“CEMS”) for each unit includes an extractive stack probe, a catalyst inlet probe for Nox , a sample handling system, and analysis rack.  The probes extract a representative sample of flue gas for transport, conditioning and analysis.  The CEMS measures and records data from the CO, Nox , and O2 analyzers.  The CEMS equipment for both units is contained in one common, climate controlled shelter located between the bases of the two stacks.  The CEMS use programmable logic controllers to interface between the analyzers and the data acquisition and handling system, which archives data and generates reports for both units.  The Nox  signal from the catalyst inlet probe is transmitted to the unit control system for input to the combustion turbine and catalyst ammonia injection controls.

Fuel Systems:

Natural Gas System

The natural gas system conveys fuel gas from the BUG meter station at the Project boundary to the combustion turbine fuel control system connections.  The system includes two electric motor driven compressors to boost the gas pressure when required, two coalescing filters to remove contaminants, and two regulator valves for final pressure control.  These components are arranged in two parallel trains, each with the capacity to feed one combustion turbine.  To provide redundancy, there is a cross connect downstream of the filters and ahead of the regulating valves.

Fuel Oil System

The fuel oil system conveys distillate fuel oil from the barge unloading station to the combustion turbine fuel oil skid connections.  Intermediate storage is provided by a storage tank at the barge unloading area and a day tank immediately outside the power plant building.  The oil is pumped from the 1,167,600 gallon barge to the 350,000 gallon storage tank by diesel engine driven pumps on the barge.  The electric motor driven fuel oil forwarding pumps move the oil to the 5,800 gallon day tank from the storage tank and the electric motor driven fuel oil supply pumps move the oil from the day tank to the fuel oil injection pumps on the combustion turbine fuel oil skid.  An electric header is provided between the supply pumps and the fuel oil skid.  Return oil from the fuel oil skid is piped to the day tank.

Electric Generators:

Combustion Turbine Generators

The TEWAC generators were manufactured by SPC and each generator is rated at 125 MVA at 0.85 power factor with a generator cooling air temperature of 40ºC at corresponding closed cooling water supply temperature of approximately 24ºC nominal.  Therefore, the generators supplied for BNY are sufficient to handle the maximum turbine output at site conditions.

Steam Turbine Generators

The generators were manufactured by Electric Machinery Company and are rated at 47,430 kVA at a 0.85 power factor.  These generators are of the TEWAC design and, therefore, the actual capacity is dependent on the cooling water temperature.  The plant heat balances prepared by Parsons Main show a cooling water temperature of 75ºF for the spring to fall condition.  The steam turbine is expected to be operated at its highest load during the summer due to reduced demand for export steam.  At this temperature, the Class B rating of the generator is 44 MW, which is sufficient for the turbine maximum rating of 40 MW.

Electrical and Control Systems:

Normal Station Service Power

Power is generated on site and can also be received to assist in the shutdowan operations of the Project.  Electrical power is received and furnished through Con Ed’s transmission system at 138 kV.  When the Project is operating, it furnishes all its electric power needs.  Alternatively, when both trains are not operational (e.g., down for maintenance) electric power is supplied through either or both main transformers.  Electrical power is generated at 13.8 kV and then transformed from 13.8 kV to 4,160 V to 480 V and lower voltage levels suitable for equipment needs.

Emergency Power

Emergency power systems also exist to assist plant operations.  The emergency systems include diesel generators, uninterruptible power supplies, and direct current (“DC”) power.  Emergency power provides an alternative source for station power requirements, should Con Ed’s power not be available.  Uninterruptible power and DC/battery power are provided for equipment that must operate under all conditions, such as lube oil pumps and turning gear to ensure a proper cool down process of the turbines during an emergency trip.

Transmission

Electrical power generated through the combustion and steam turbine generators at 13.8 kV is transformed to 138 kV for delivery to Con Ed.  Two main transformers are provided for this service.  Each transformer is dedicated to a combustion turbine generator and steam turbine generator.  In addition, two additional transformers provide power to BNYDC at 13.8 kV.

Control Systems

The process control system consists of two distinct and inter-relating control systems.  One system is dedicated to the starting, normal operation, and shutdown of the combustion turbines.  This system, furnished by SPC, the combustion turbine manufacturer, also provides status information to the steam plant DCS.

Each combustion and steam turbine is provided with its own control system.  The DCS provides for the control and monitoring of the boilers and auxiliaries, and integration of these with the turbine control systems.  The DCS is manufactured by Bailey Controls and provides control, monitoring, alarm reporting, and performance reporting of the steam plant and auxiliary systems.

Water and Wastewater:

Circulating Water System

The circulating water system provides cooling water to the condenser and consists of three circulating water pumps.  Two pumps are required to operate in support of normal plant operation.  Circulating water is drawn from and returned to the East River through underground intake and discharge tunnels.  The circulation water pumps and equipment associated with this system are consistent with the type of equipment seen in power generation facilities.  The circulation water system also uses two 100% capacity seawater booster pumps to provide cooling water to the closed loop cooling water system.  The seawater booster pumps take suction from the circulating water supply header, pump cooling water through the closed cooling water heat exchangers, and discharge to the circulating water discharge tunnel.

Water Supply

BNY requires water for cooling and for process makeup.  Cooling water is supplied on a once through basis from East River intakes.  Process makeup water is primarily used as makeup to the HRSG, to support the generation of steam for various in-plant uses and off-site steam sales, and for water injection into the combustion turbines to reduce NO x emissions when firing oil.

BNY has a continuous maximum design steam production requirement of 2,800 gpm, as outlined in Table 3.1.  Actual steam production required from the facility varies with each season varying from a peak requirement in the winter heating season to a minimum I the spring/fall.

The source for BNY makeup water to BNYCP facility is the New York City municipal water supply.  The city municipal supply has been demonstrated to be available to BNY in sufficient quantities to meet the maximum design makeup requirement.  All wastewater generated by BNY is discharged to the municipal sewer system.

To meet the feedwater chemistry limits of the HRSG and ultimately the strict steam quality requirement of the Con Ed ESA, the municipal supply water must be chemically treated to remove all dissolved salts, organic compounds, and any suspended solids.  The required treatment of the city water supply was provided under contract by Ecolochem.  The Ecolochem treatment system consisted of redundant trailer-mounted water treatment systems that are ganged together to meet the total process makeup water demand.  The trailer-mounted water treatment systems must be renewed or regenerated upon exhaustion of the filtering capacity.  Upon exhaustion, the treatment trailers are removed from the site and replaced with fresh treatment trailers.  The treatment trailers are regenerated at an off-site facility under the Ecolochem contract.

Table 3.1

	Steam

Destination

Customer
	Design

Steam

(lbs/hr)
	Design

Flow

(gpm)
	Winter Flow Max.

(gpm)


	Winter Flow Avg.  (gpm)
	Summer Flow Avg. (gpm)
	Summer Flow Avg. (gpm)
	Spring

/Fall

Flow

(gpm)
	Min Flow

	Con Ed
	1,000,000
	2,000
	1,600
	1,700
	1,100
	1,100
	1,500
	N/A

	Siemens GT
	200,000
	400
	400
	0
	400
	400
	0
	N/A

	BNYDC
	100,000
	200
	200
	60
	200
	0
	0
	N/A

	Red Hook
	60,000
	120
	120
	40
	120
	30
	30
	N/A

	HRSC

Blowdown
	35,000
	70
	70
	70
	70
	70
	70
	N/A

	Totals
	1,395,000
	2,790
	2,390
	1,870
	1,890
	1,600
	1,600
	800


To reduce the annual cost of the Ecolochem contracted services, BYNCP has investigated a number of alternative water treatment concepts and at least one alternative water supply.  As a result of these investigations, BNYCP decided to replace the existing Ecolochem contracted treatment trailers with a permanent on-site water treatment system which continues to use city water.  This new system was constructed under a Design/Build Agreement with Illinois Water Treatment, Inc. (U.S. Filter), a wholly owned subsidiary of United States Filter Corporation.

The new Water Treatment System is a very conservative design for the treatment of potable city water.  The treatment system incorporates the advanced technologies of micro-filtration, reverse osmosis and mixed bed ion exchange to produce demineralized water.  The new Water Treatment System will be housed in a dedicated building to be constructed on the BNY site of the BNYCP facility and will be sized to meet continuously a peak design flow of 2,800 gpm.  The quality of the finished water should meet BNY requirements.  U.S. Filter is one of the largest U.S. based water treatment systems contractors and is experienced in the design, construction and operation of water treatment systems for utility and industrial facilities.

The total lump sum cost of the Design/Build Agreement is $15,597,400.  This covers the total construction cost of the Water Treatment System including the building to house the new system, exclusive of spare parts.  The required spare parts will be purchased separately from U.S. Filter as part of the normal procurement cycle.

Based on the contract documents, the new Water Treatment System was projected to produce treated makeup water at a cost of between $2.76 to $3.02 per 1000 gallons, depending on which of the two alternative U.S. Filter water treatment process designs are selected by BNYCP.  The operating costs projected by U.S. Filter are reasonable for the Water Treatment System proposed.  Compared to the present cost of the Ecolochem treatment trailers, estimated at $4.44 per 1,000 gallons, the new Water Treatment System provides a projected cost savings of $1.42 to $1.68 per 1,000 gallons.  Actual savings may be slightly less since the projected costs do not appear to include operating and maintenance labor or the project financing costs.  The largest single operating cost item for the production of treated makeup water will be the purchase of potable city water which accounts for fully 50% of the total production cost from the new Water Treatment System.  To address the significant impact of the cost of City water on operating expenses, BNYCP previously studies an option of using treated wastewater from Red Hook as the source water for BNY.  BNYCP has since rejected the option of using the Red Hook treated wastewater.  However, the new Water Treatment System as designed by U.S. Filter, may be capable of using the Red Hook effluent as the source water if it is economically attractive.  Stone & Webster expected that before any consideration is given to the Red Hook effluent, sufficient pilot testing be conducted to fully determine whether the treated product from the Water Treatment System is fully in compliance with the Con Ed ESA and its steam chemistry restrictions.

Wastewater System

The wastewater system is of typical design for this type of facility.  The system is comprised of two major subsystems:  general drainage and HRSG blow down.  The general floor drains go to a dedicated sump which is then pumped to an oil water separator which allows for drainage to the city sewer system or for transfer off site for treatment.  Steam blow downs and HRSG drains go to a dedicated sump which is piped directly to the six foot sewer main.

ATTACHMENT

B

OWNERSHIP STRUCTURE 

ATTACHMENT

C

O&M ORGANIZATION 

AND COST ANALYSIS

[image: image2.wmf]Operations & Maintenance Report

Brooklyn Navy Yard Facility, New York

2 x Siemens V84.2, CC-Cogen, 286MW

[image: image3.png]



By

Karl Masani

Enron Engineering & Operational Services

May 29, 2001

Table of Contents
1.0 O&M Trip Report

· Facility Description & Summary

· Gas Turbines

· Heat Recovery Steam Generators

· Steam Turbines

· Emissions Control Equipment

· Fuel Systems

· Water & Wastewater Systems

· O&M Contract

· O&M Budget

· Major Maintenance reserve per Enron

2.0 BNY Monthly Report April 2001

3.0 BNY Financials & Detailed O&M Budget for 2001 

4.0 BNY Major Maintenance Reserve

5.0 BNY O&M Agreement 

6.0 BNY O&M Incentive Package for Palmark 

7.0 BNY Performance Spreadsheets (1997-2001)

8.0 Stone & Webster Report for BNY, 1998

9.0 Boiler Inspection Reports

10.0 Site Contacts and Location

[image: image4.png]


Section 1:  Trip Report

A trip was scheduled for May 24, 2001 to the Brooklyn Navy Yard for facility evaluation purposes.  Due to time constraints, a detailed O&M evaluation could not be conducted.

Enron Team:  Dan Williams, Bill Keeney, Greg Martin, Karl Masani, Bill Curra

Brooklyn Navy Yard Team:  Maria Rigatti (Edison Mission), Mike Brown (Palmark)

Facility Description & Summary

Brooklyn Navy Yard (BNY) is a combined cycle, cogeneration power plant nominally rated at 286MW at ISO conditions when producing electric power.  The facility comprises of the following:

· 2xSiemens V84.2 combustion turbine generator sets with DLN combustors.  Each is rated at 103MW.

· 2xABB unfired, natural circulation boilers with 3 pressure levels and an integral deaerator.

· 2xSiemens extraction, condensing Steam Turbines nominally rated at 40MW.

· A water treatment facility with RO and Mixed Bed Demin units (will be officially commissioned in June, 2001).


BNY is located on a 6.8-acre site in the Brooklyn Navy Yard in Brooklyn, New York.  The site is at the edge of a ship basin off the East River and is leased from the BNYDC.  BNY is currently owned by Edison Mission and York Research and is operated by a third party operator, Palmark Inc.  BNY went commercial on November 1, 1996.   The facility is currently being operated on baseload with full steam export.

Major Risk:

· BNY has had major tube leaks in both boilers due boiler materials and design.  BNY is considering re-tubing 60% of both boilers at a cost of $6 million each.

Major Equipment

1. Gas Turbines & Generators

The plant is equipped with 2 Siemens V84.2 combustion units with a nominal rating of 103MW each.  The V84.2 is a scaled down version of the V94, 50 Hz machine.  The V84.2 has a 17 stage compressor that produces a compression ratio of 11:1, two silo type combustion units with gas and oil burners, and a four‑stage turbine with a nominal inlet temperature of 2,020°F. The totally enclosed water to air cooled ("TEWAC") generator is connected to the compressor end of the rotor and the exhaust exits axially from the turbine end. Each combustion turbine generator is provided with an electronic turbine control system, combined vibration monitoring system, combined tube and control oil system, generator static excitation system, and generator static starting system.

2. Heat Recovery Steam Generator

The exhaust of each combustion turbine is ducted to an HRSG provided by Asea Brown Boveri/Combustion Engineering.  From this 1,000°F exhaust gas, the HRSG produces steam at three pressure levels, 936 pounds per square inch gauge ("psig"), 121 psig, and 25 psig. The high pressure ("HP") steam is used to generate electricity in the steam turbine, for combustion turbine steam injection, and to supply export steam. The intermediate pressure ("IP") steam is supplied to the steam turbine to produce additional electricity and to supply export steam. The low pressure steam ("LP") is used in the integral deaerator to pre‑heat and deoxygenate the HRSG feedwater.

3.
Steam Turbine

Siemens supplied two steam turbine and generator sets for the project. Each has a rating of 10 MW with full extraction and 40 MW without extraction. To provide flexibility for export steam operations, each steam turbine is provided with intermediate extraction and admission ports in addition to the normal main steam inlet and condenser exhaust connections.  In normal operation, main steam is provided from the high pressure section of the HRSG, extraction steam is exported for sale, and admission steam is provided from the intermediate pressure section of the HRSG.  Each steam turbine generator is provided with an electrohydraulic turbine control system, combined vibration monitoring system, combined lube oil system with coolers and purifier, generator cooling system, and generator static excitation system.

4. Emission Control Equipment

Gas Turbines
The gas burners are the Siemens hybrid pre mix design that can produce low NOx levels (9 ppm is guaranteed) without steam or water injection when burning gas. The gas burners operate in pre-mix mode at power levels above 70%. The oil burners are a normal diffusion design and require water injection to limit NOx to 42 ppm when burning oil.  In other V84.2 power plants which were cycled below full load, the pre mix burners were not fully reliable. Base loaded V84.2s, however, such as the BNY, are running successfully in pre mix mode. Siemens has had problems with V84.2 units switching between gas and oil firing because power must be reduced to about 70% for fuel switching which can affect the reliability of the fuel switching valves in the fuel oil system. However the BNY machines are not expected to have to switch fuels often due to the Project's limited operation on fuel oil. Therefore fuel switching is not expected to have a significant impact on Project performance.

Catalyst Systems

Separate catalyst systems are provided in each HRSG to control the emissions of NOx and CO. Each catalyst bed is designed for full load exhaust gas flow and is located in its associated HRSG module to assure proper operating temperature. Provisions are made for periodic replacement of the catalyst beds as dictated by catalyst performance.  

In the SCR, aqueous ammonia is injected into the exhaust gas stream in vapor form, ahead of the catalyst, through a grid system that is designed to assure even distribution. The NOx catalyst selectively reduces the NOx to nitrogen and water with the use of an ammonia reagent. The SCR system is designed to provide a stack outlet NOx concentration of less than 3.5 ppm with an inlet concentration of no greater than 9 ppm. When firing oil, the SCR is capable of reducing the 42 ppm in the exhaust gas to less than 10 ppm. In order to reduce the exhaust CO concentration to permit limits and to prevent fouling of the downstream heat transfer surfaces the facility also includes a CO catalyst which directly oxides CO to C02 without the need for any chemical reagents.

CEMS

The Continuous Emissions Monitoring System ("CEMS") for each unit includes an extractive stack probe, a catalyst inlet probe for NOx, a sample handling system, and analysis rack. The probes extract a representative sample of flue gas for transport, conditioning and analysis. The CEMS measures and records data from the CO, NOx, and O2 analyzers. The CEMS equipment for both units is contained in one common, climate controlled shelter located between the bases of the two stacks. The CEMS use programmable logic controllers to interface between the analyzers and the data acquisition and handling system, which archives data and generates reports for both units. The NOx signal from the catalyst inlet probe is transmitted to the unit control system for input to the combustion turbine and catalyst ammonia injection controls.

5.
Fuel Systems

Natural Gas System

The natural gas system conveys fuel gas from the meter station at the facility boundary to the combustion turbine fuel control system connections. The system includes two electric motor driven compressors to boost the gas pressure when required, two coalescing filters to remove contaminants, and two regulator valves for final pressure control. These components are arranged in two parallel trains, each with the capacity to feed one combustion turbine. To provide redundancy, there is across connect downstream of the filters and ahead of the regulating valves.

Fuel Oil System

The fuel oil system conveys distillate fuel oil from the barge unloading station to the combustion turbine fuel oil skid connections.  Intermediate storage is provided by a storage tank at the barge unloading area and a day tank immediately outside the power plant building.  The oil is pumped from the 1,167,600 gallon barge to the 350,000 gallon storage tank by diesel engine driven pumps on the barge.  The electric motor driven fuel oil forwarding pumps move the oil to the 5,800 gallon day tank from the storage tank and the electric motor driven fuel oil supply pumps move the oil from the day tank to the fuel oil injection pumps on the combustion turbine fuel oil skid.  An electric heater is provided between the supply pumps and the fuel oil skid.  Return oil from the fuel oil skid is piped to the day tank.

6.
Water and Wastewater Systems

Circulating Water System

The circulating water system provides cooling water to the condenser and consists of three circulating water pumps.  Two pumps are required to operate in support of normal plant operation. Circulating water is drawn from and returned to the East River through underground intake and discharge tunnels.  The circulating water system also uses two 100% capacity seawater booster pumps to provide cooling water to the closed loop cooling water system.  The seawater booster pumps take suction from the circulating water supply header, pump cooling water through the closed cooling water heat exchangers, and discharge to the circulating water discharge tunnel. 

Water Supply

BNY requires water for cooling and for process makeup.  Cooling water is supplied on a once through basis from East River intakes.  Process makeup water is primarily used as makeup to the HRSG, to support the generation of steam for various in‑plant uses and off‑site steam sales, and for water injection into the combustion turbines to reduce NOx emissions when firing oil.

BNY has a continuous maximum design steam production requirement of 2,800 gpm. Actual steam production required from the facility varies with each season varying from a peak requirement in the winter heating season to a minimum in the spring/fall.

The source for BNY makeup water is the New York City municipal water supply. The city municipal supply has been demonstrated to be available to BNY in sufficient quantities to meet the maximum design makeup requirement. All wastewater generated by BNY is discharged to the municipal sewer system.

To meet the feedwater chemistry limits of the HRSG and ultimately the strict steam quality requirements of the Con Ed ESA, the municipal supply water must be chemically treated to remove all dissolved salts, organic compounds, and any suspended solids.  The required treatment of the city water supply was provided under contract by Ecolochem.  BNY is in the process of commissioning a water treatment facility consisting of reverse osmosis and mixed bed demineralizers. 

7.
O&M Contract


The facility is currently being operated and maintained by Palmark, which is a wholly owned subsidiary of Primesouth, Inc.  A complete O&M staff of 37 employees are presently employed on site of which some are union.  The annual O&M fee is approximately $400,000 and is based on the number of employees employed on site.  The maximum LOL is one-third of the management fee paid to Palmark plus any incentive fee.  An operator incentive program was also negotiated.

8. O&M Budget

A detailed budget was provided to us by Palmark for the year 2001.  This budget is based on 5 years of historical cost information and is a comprehensive budget.  It is attached to the financial section of this report.  Palmark also forecasted major maintenance till 2007 and is also included in this report.

	
	Scheduled Gas Turbine Maintenance Costs  ( 30 Year-Quarterly)
	

	
	2 X SW-V84.2-V0
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	Cumulative EOH (or EOS)
	Year
	Initial
	1996
	1997
	1998
	1999
	2000
	2001
	2002

	 
	 
	Initial
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	CTG 1
	 
	 
	6000
	16000
	26000
	36000
	46000
	56000
	66000

	CTG 2
	 
	7500
	17500
	27500
	37500
	47500
	57500
	67500
	77500

	CTG 3
	 
	 
	 
	 
	 
	 
	 
	 
	 

	CTG 4
	 
	 
	 
	 
	 
	 
	 
	 
	 

	CTG 5
	 
	 
	 
	 
	 
	 
	 
	 
	 

	CTG 6
	 
	 
	 
	 
	 
	 
	 
	 
	 

	CTG 7
	 
	 
	 
	 
	 
	 
	 
	 
	 

	CTG 8
	 
	 
	 
	 
	 
	 
	 
	 
	 

	CTG 9
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Maintenance Schedule
	 
	 
	1996
	1997
	1998
	1999
	2000
	2001
	2002

	 
	 
	 
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	CTG 1
	 
	
	----
	CI---
	CI--CI
	--HGPI-
	--CI-
	-
	CI--HGPI

	CTG 2
	 
	
	CI--CI
	--CI-
	--HGPI-
	-CI--
	CI---
	HGPI
	--CI-

	CTG 3
	 
	
	----
	----
	----
	----
	----
	-
	----

	CTG 4
	 
	
	----
	----
	----
	----
	----
	-
	----

	CTG 5
	 
	
	----
	----
	----
	----
	----
	-
	----

	CTG 6
	 
	
	----
	----
	----
	----
	----
	-
	----

	CTG 7
	 
	
	----
	----
	----
	----
	----
	-
	----

	CTG 8
	 
	
	----
	----
	----
	----
	----
	-
	----

	CTG 9
	 
	
	----
	----
	----
	----
	----
	-
	----

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	
	
	

	labor Cost for Turbine (K$)
	 
	 
	68.0
	68.0
	1,243.0
	1,209.0
	68.0
	1,243.0
	1,243.0

	
	
	
	
	
	
	
	
	
	

	Parts Replace 
	New (K$)
	Initial
	1996
	1997
	1998
	1999
	2000
	2001
	2002

	 
	K$
	 
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	Row 1 Blade
	567.7
	567.7
	 
	 
	 
	 
	 
	 
	 

	Row 2 Blade
	734.7
	734.7
	 
	 
	 
	 
	 
	 
	 

	Row 3 Blade
	614.6
	 
	 
	 
	 
	 
	 
	614.6
	 

	Row 4 Blade
	660.4
	 
	 
	 
	 
	 
	 
	 
	 

	Row 1 Vane
	828.5
	828.5
	 
	 
	 
	 
	 
	 
	 

	Row 2 Vane
	624.4
	624.4
	 
	 
	 
	 
	 
	 
	 

	Row 3 Vane
	722.4
	 
	 
	 
	722.4
	 
	 
	 
	 

	Row 4 Vane
	871.9
	 
	 
	 
	 
	 
	 
	 
	 

	Dampening Rings
	20.7
	 
	 
	 
	20.7
	20.7
	 
	20.7
	20.7

	Mixing Elbows
	525.3
	 
	 
	 
	525.3
	 
	 
	 
	 

	Seal Rings
	103.2
	 
	 
	 
	103.2
	103.2
	 
	103.2
	103.2

	Transition Rings
	29.4
	 
	 
	 
	29.4
	29.4
	 
	29.4
	29.4

	Tiles & Hardware
	34.6
	 
	 
	 
	34.6
	34.6
	 
	34.6
	34.6

	Compressor Blades
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Compressor Vanes
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Mixing Elbow Hardware
	35.3
	 
	 
	 
	35.3
	35.3
	 
	35.3
	35.3

	Inner Casing Hardware
	14.4
	 
	 
	 
	14.4
	14.4
	 
	14.4
	14.4

	Miscellaneous Hardware
	55.0
	 
	 
	 
	55.0
	55.0
	 
	55.0
	55.0

	Locking Plate Hardware
	54.1
	 
	 
	 
	54.1
	54.1
	 
	54.1
	54.1

	Casing Inspection
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Inner Casing
	1,964.7
	 
	 
	 
	 
	 
	 
	1,964.7
	 

	Casing Upgrade (old to new)
	783.8
	 
	 
	 
	 
	 
	 
	 
	783.8

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Generator field
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Generator stator
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Consumable for Minor
	33.3
	 
	66.5
	66.5
	99.8
	66.5
	66.5
	99.8
	99.8

	Consumable for HGPI
	183.3
	 
	 
	 
	183.3
	183.3
	 
	183.3
	183.3

	Consumable for Major
	 
	 
	 
	 
	 
	 
	 
	 
	 

	end
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	end
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	
	
	 
	
	
	
	
	
	
	

	Sub-Total Parts  (K$)
	
	2,755.3
	66.5
	66.5
	1,877.5
	596.5
	66.5
	3,209.0
	1,413.5

	Parts     (with Discount)
	 
	
	66.5
	66.5
	1,877.5
	596.5
	66.5
	3,209.0
	1,413.5

	Total Parts (w Freight)
	2%
	
	67.8
	67.8
	1,915.0
	608.4
	67.8
	3,273.2
	1,441.7

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	Parts Repair
	Repair
	 
	1996
	1997
	1998
	1999
	2000
	2001
	2002

	 
	(K$)
	 
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	Row 1 Blade
	94.8
	 
	 
	 
	94.8
	94.8
	 
	94.8
	 

	Row 2 Blade
	122.0
	 
	 
	 
	122.0
	122.0
	 
	122.0
	 

	Row 3 Blade
	75.1
	 
	 
	 
	 
	 
	 
	75.1
	75.1

	Row 4 Blade
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Row 1 Vane
	163.7
	 
	 
	 
	163.7
	163.7
	 
	163.7
	 

	Row 2 Vane
	214.3
	 
	 
	 
	214.3
	214.3
	 
	214.3
	 

	Row 3 Vane
	70.7
	 
	 
	 
	70.7
	70.7
	 
	70.7
	70.7

	Row 4 Vane
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Dampening Rings
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Mixing Elbows
	146.5
	 
	 
	 
	146.5
	146.5
	 
	146.5
	 

	Seal Rings
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Transition Rings
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Tiles & Hardware
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Compressor Blades
	20.8
	 
	 
	 
	20.8
	20.8
	 
	20.8
	20.8

	Compressor Vanes
	13.0
	 
	 
	 
	13.0
	13.0
	 
	13.0
	13.0

	Mixing Elbow Hardware
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Inner Casing Hardware
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Miscellaneous Hardware
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Locking Plate Hardware
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Casing Inspection
	25.3
	 
	 
	 
	25.3
	25.3
	 
	25.3
	25.3

	Inner Casing
	101.5
	 
	 
	 
	 
	 
	 
	 
	 

	Casing Upgrade (old to new)
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Generator field
	60.0
	 
	 
	 
	60.0
	60.0
	 
	60.0
	60.0

	Generator stator
	35.0
	 
	 
	 
	35.0
	35.0
	 
	35.0
	35.0

	Consumable for Minor
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Consumable for HGPI
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Consumable for Major
	 
	 
	 
	 
	 
	 
	 
	 
	 

	end
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	end
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	
	
	

	Sub-Total Repairs (K$)
	
	 
	
	
	966.0
	966.0
	
	1,041.1
	299.9

	Repairs     (with Discount)
	 
	
	
	
	966.0
	966.0
	
	1,041.1
	299.9

	Total Repairs (w Freight)
	2%
	
	
	
	985.3
	985.3
	
	1,061.9
	305.9

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	 
	
	 
	1996
	1997
	1998
	1999
	2000
	2001
	2002

	TOTAL new parts, repair & Labor
	
	135.8
	135.8
	4,143.3
	2,802.7
	135.8
	5,578.2
	2,990.7

	Other Relative Annual Costs (FOD Damage)
	 
	 
	 
	 
	 
	428.3
	 

	
	
	
	
	
	
	
	
	
	

	Grand Total
	
	
	135.8
	135.8
	4,143.3
	2,802.7
	135.8
	6,006.4
	2,990.7

	
	
	
	
	
	
	
	
	
	


	
	
	
	
	
	
	
	

	
	
	
	
	
	 
	
	

	
	
	
	
	
	
	
	

	2002
	2003
	2004
	2005
	2006
	2007
	2008
	2009

	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	66000
	76000
	86000
	96000
	106000
	116000
	126000
	136000

	77500
	88500
	98500
	108500
	118500
	128500
	138500
	148500

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	2002
	2003
	2004
	2005
	2006
	2007
	2008
	2009

	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	CI--HGPI
	---CI
	--CI-
	-CI--
	-HGPI--
	CI--CI
	---CI
	--HGPI-

	--CI-
	-CI--
	CI---
	HGPI--CI
	--CI-
	--CI-
	-HGPI--
	CI--CI

	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----

	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	

	1,243.0
	68.0
	68.0
	1,243.0
	1,209.0
	102.0
	1,209.0
	1,243.0

	
	
	
	
	
	
	
	

	2002
	2003
	2004
	2005
	2006
	2007
	2008
	2009

	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	 
	 
	 
	567.7
	567.7
	 
	567.7
	 

	 
	 
	 
	734.7
	734.7
	 
	734.7
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	660.4
	660.4
	 
	 
	 

	 
	 
	 
	828.5
	828.5
	 
	828.5
	 

	 
	 
	 
	624.4
	624.4
	 
	624.4
	 

	 
	 
	 
	 
	 
	 
	 
	722.4

	 
	 
	 
	871.9
	871.9
	 
	 
	 

	20.7
	 
	 
	20.7
	20.7
	 
	20.7
	20.7

	 
	 
	 
	525.3
	525.3
	 
	525.3
	 

	103.2
	 
	 
	103.2
	103.2
	 
	103.2
	103.2

	29.4
	 
	 
	29.4
	29.4
	 
	29.4
	29.4

	34.6
	 
	 
	34.6
	34.6
	 
	34.6
	34.6

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	35.3
	 
	 
	35.3
	35.3
	 
	35.3
	35.3

	14.4
	 
	 
	14.4
	14.4
	 
	14.4
	14.4

	55.0
	 
	 
	55.0
	55.0
	 
	55.0
	55.0

	54.1
	 
	 
	54.1
	54.1
	 
	54.1
	54.1

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	783.8
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	99.8
	66.5
	66.5
	99.8
	66.5
	99.8
	66.5
	99.8

	183.3
	 
	 
	183.3
	183.3
	 
	183.3
	183.3

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	

	1,413.5
	66.5
	66.5
	5,442.7
	5,409.5
	99.8
	3,877.1
	1,352.1

	1,413.5
	66.5
	66.5
	5,442.7
	5,409.5
	99.8
	3,877.1
	1,352.1

	1,441.7
	67.8
	67.8
	5,551.6
	5,517.7
	101.7
	3,954.7
	1,379.2

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	2002
	2003
	2004
	2005
	2006
	2007
	2008
	2009

	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	 
	 
	 
	 
	 
	 
	94.8
	94.8

	 
	 
	 
	 
	 
	 
	122.0
	122.0

	75.1
	 
	 
	 
	 
	 
	75.1
	75.1

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	163.7
	163.7

	 
	 
	 
	 
	 
	 
	214.3
	214.3

	70.7
	 
	 
	70.7
	70.7
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	146.5
	146.5

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	20.8
	 
	 
	20.8
	20.8
	 
	20.8
	20.8

	13.0
	 
	 
	13.0
	13.0
	 
	13.0
	13.0

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	25.3
	 
	 
	25.3
	25.3
	 
	25.3
	25.3

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	60.0
	 
	 
	60.0
	60.0
	 
	60.0
	60.0

	35.0
	 
	 
	35.0
	35.0
	 
	35.0
	35.0

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	

	299.9
	
	
	224.8
	224.8
	
	970.4
	970.4

	299.9
	
	
	224.8
	224.8
	
	970.4
	970.4

	305.9
	
	
	229.3
	229.3
	
	989.8
	989.8

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	2002
	2003
	2004
	2005
	2006
	2007
	2008
	2009

	2,990.7
	135.8
	135.8
	7,023.9
	6,956.0
	203.7
	6,153.5
	3,612.0

	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	

	2,990.7
	135.8
	135.8
	7,023.9
	6,956.0
	203.7
	6,153.5
	3,612.0

	
	
	
	
	
	
	
	


	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	2010
	2011
	2012
	2013
	2014
	2015
	2016
	2017
	2018

	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	146000
	156000
	166000
	176000
	186000
	196000
	206000
	216000
	226000

	158500
	168500
	178500
	188500
	198500
	208500
	218500
	228500
	238500

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	2010
	2011
	2012
	2013
	2014
	2015
	2016
	2017
	2018

	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	-CI--
	CI---
	CI--HGPI
	--CI-
	--CI-
	-CI--
	HGPI---
	CI--CI
	--CI-

	---CI
	--HGPI-
	-CI--
	-CI--
	CI--HGPI
	---CI
	--CI-
	-CI--
	HGPI---

	----
	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----
	----

	----
	----
	----
	----
	----
	----
	----
	----
	----

	 
	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	
	

	68.0
	1,209.0
	1,243.0
	68.0
	1,243.0
	68.0
	1,209.0
	102.0
	1,209.0

	
	
	
	
	
	
	
	
	

	2010
	2011
	2012
	2013
	2014
	2015
	2016
	2017
	2018

	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	 
	 
	 
	 
	567.7
	 
	567.7
	 
	567.7

	 
	 
	 
	 
	734.7
	 
	734.7
	 
	734.7

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	660.4
	 
	660.4
	 
	 

	 
	 
	 
	 
	828.5
	 
	828.5
	 
	828.5

	 
	 
	 
	 
	624.4
	 
	624.4
	 
	624.4

	 
	722.4
	722.4
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	871.9
	 
	871.9
	 
	 

	 
	20.7
	20.7
	 
	20.7
	 
	20.7
	 
	20.7

	 
	 
	 
	 
	525.3
	 
	525.3
	 
	525.3

	 
	103.2
	103.2
	 
	103.2
	 
	103.2
	 
	103.2

	 
	29.4
	29.4
	 
	29.4
	 
	29.4
	 
	29.4

	 
	34.6
	34.6
	 
	34.6
	 
	34.6
	 
	34.6

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	35.3
	35.3
	 
	35.3
	 
	35.3
	 
	35.3

	 
	14.4
	14.4
	 
	14.4
	 
	14.4
	 
	14.4

	 
	55.0
	55.0
	 
	55.0
	 
	55.0
	 
	55.0

	 
	54.1
	54.1
	 
	54.1
	 
	54.1
	 
	54.1

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	66.5
	66.5
	99.8
	66.5
	99.8
	66.5
	66.5
	99.8
	66.5

	 
	183.3
	183.3
	 
	183.3
	 
	183.3
	 
	183.3

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	
	

	66.5
	1,318.9
	1,352.1
	66.5
	5,442.7
	66.5
	5,409.5
	99.8
	3,877.1

	66.5
	1,318.9
	1,352.1
	66.5
	5,442.7
	66.5
	5,409.5
	99.8
	3,877.1

	67.8
	1,345.3
	1,379.2
	67.8
	5,551.6
	67.8
	5,517.7
	101.7
	3,954.7

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	2010
	2011
	2012
	2013
	2014
	2015
	2016
	2017
	2018

	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4
	Q4

	 
	94.8
	 
	 
	 
	 
	 
	 
	94.8

	 
	122.0
	 
	 
	 
	 
	 
	 
	122.0

	 
	 
	 
	 
	75.1
	 
	75.1
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	163.7
	 
	 
	 
	 
	 
	 
	163.7

	 
	214.3
	 
	 
	 
	 
	 
	 
	214.3

	 
	 
	70.7
	 
	70.7
	 
	70.7
	 
	70.7

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	146.5
	 
	 
	 
	 
	 
	 
	146.5

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	20.8
	20.8
	 
	20.8
	 
	20.8
	 
	20.8

	 
	13.0
	13.0
	 
	13.0
	 
	13.0
	 
	13.0

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	25.3
	25.3
	 
	25.3
	 
	25.3
	 
	25.3

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	60.0
	60.0
	 
	60.0
	 
	60.0
	 
	60.0

	 
	35.0
	35.0
	 
	35.0
	 
	35.0
	 
	35.0

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	
	

	
	895.3
	224.8
	
	299.9
	
	299.9
	
	966.0

	
	895.3
	224.8
	
	299.9
	
	299.9
	
	966.0

	
	913.2
	229.3
	
	305.9
	
	305.9
	
	985.3

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	2010
	2011
	2012
	2013
	2014
	2015
	2016
	2017
	2018

	135.8
	3,467.4
	2,851.5
	135.8
	7,100.5
	135.8
	7,032.6
	203.7
	6,149.0

	 
	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	
	

	135.8
	3,467.4
	2,851.5
	135.8
	7,100.5
	135.8
	7,032.6
	203.7
	6,149.0

	
	
	
	
	
	
	
	
	


	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	2019
	2020
	2021
	2022
	2023
	2024
	2025
	
	2026

	Q4
	Q1
	Q2
	Q2
	Q2
	Q2
	Q2
	
	Q4

	236000
	238500
	241000
	251000
	261000
	271000
	281000
	
	285642.8571

	248500
	251000
	253500
	263500
	273500
	283500
	293500
	
	298142.8571

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	2019
	2020
	2021
	2022
	2023
	2024
	2025
	
	2026

	Q4
	Q1
	Q2
	Q2
	Q2
	Q2
	Q2
	 
	Q4

	-HGPI--
	HGPI---
	---CI
	--CI-
	-CI--
	-HGPI--
	CI--CI
	
	-HGPI--

	CI--CI
	--CI-
	-CI--
	CI---
	HGPI--CI
	--CI-
	--CI-
	
	CI--CI

	----
	----
	----
	----
	----
	----
	----
	
	----

	----
	----
	----
	----
	----
	----
	----
	
	----

	----
	----
	----
	----
	----
	----
	----
	
	----

	----
	----
	----
	----
	----
	----
	----
	
	----

	----
	----
	----
	----
	----
	----
	----
	
	----

	----
	----
	----
	----
	----
	----
	----
	
	----

	----
	----
	----
	----
	----
	----
	----
	
	----

	 
	 
	 
	 
	 
	 
	 
	
	 

	
	
	
	
	
	
	
	 
	

	1,243.0
	1,209.0
	68.0
	68.0
	1,243.0
	1,209.0
	102.0
	21,845.0
	11,048.9

	
	
	
	
	
	
	
	
	

	2019
	2020
	2021
	2022
	2023
	2024
	2025
	
	2026

	Q4
	Q1
	Q2
	Q2
	Q2
	Q2
	Q2
	
	Q4

	 
	 
	 
	 
	 
	 
	 
	3,406.4
	1,703.2

	 
	 
	 
	 
	 
	 
	 
	4,408.2
	2,204.1

	 
	 
	 
	 
	 
	614.6
	 
	1,229.3
	790.2

	 
	 
	 
	 
	 
	 
	 
	2,641.6
	1,320.8

	 
	 
	 
	 
	 
	 
	 
	4,971.1
	2,485.5

	 
	 
	 
	 
	 
	 
	 
	3,746.3
	1,873.2

	 
	 
	 
	 
	 
	 
	 
	2,889.7
	1,444.8

	 
	 
	 
	 
	 
	 
	 
	3,487.8
	1,743.9

	20.7
	20.7
	 
	 
	20.7
	20.7
	 
	352.5
	177.7

	 
	 
	 
	 
	 
	 
	 
	3,677.3
	1,838.6

	103.2
	103.2
	 
	 
	103.2
	103.2
	 
	1,754.2
	884.5

	29.4
	29.4
	 
	 
	29.4
	29.4
	 
	499.4
	251.8

	34.6
	34.6
	 
	 
	34.6
	34.6
	 
	588.5
	296.7

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	35.3
	35.3
	 
	 
	35.3
	35.3
	 
	600.5
	302.8

	14.4
	14.4
	 
	 
	14.4
	14.4
	 
	244.0
	123.0

	55.0
	55.0
	 
	 
	55.0
	55.0
	 
	935.0
	471.4

	54.1
	54.1
	 
	 
	54.1
	54.1
	 
	920.0
	463.9

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	1,964.7
	982.4

	 
	 
	 
	 
	 
	 
	 
	783.8
	391.9

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	99.8
	66.5
	66.5
	66.5
	99.8
	66.5
	99.8
	2,394.0
	1,240.9

	183.3
	183.3
	 
	 
	183.3
	183.3
	 
	3,115.3
	1,570.7

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	
	
	
	
	
	
	
	 
	

	629.7
	596.5
	66.5
	66.5
	629.7
	1,211.1
	99.8
	44,609.5
	22,562.1

	629.7
	596.5
	66.5
	66.5
	629.7
	1,211.1
	99.8
	44,609.5
	22,562.1

	642.3
	608.4
	67.8
	67.8
	642.3
	1,235.3
	101.7
	45,501.7
	23,013.4

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	2019
	2020
	2021
	2022
	2023
	2024
	2025
	 
	2026

	Q4
	Q1
	Q2
	Q2
	Q2
	Q2
	Q2
	
	Q4

	94.8
	94.8
	 
	 
	94.8
	 
	 
	947.7
	453.5

	122.0
	122.0
	 
	 
	122.0
	 
	 
	1,219.8
	583.8

	 
	 
	 
	 
	 
	 
	 
	450.7
	225.4

	 
	 
	 
	 
	 
	 
	 
	
	 

	163.7
	163.7
	 
	 
	163.7
	 
	 
	1,636.9
	783.4

	214.3
	214.3
	 
	 
	214.3
	 
	 
	2,142.7
	1,025.4

	70.7
	70.7
	 
	 
	70.7
	 
	 
	919.6
	444.7

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	146.5
	146.5
	 
	 
	146.5
	 
	 
	1,464.7
	701.0

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	20.8
	20.8
	 
	 
	20.8
	20.8
	 
	353.0
	178.0

	13.0
	13.0
	 
	 
	13.0
	13.0
	 
	220.5
	111.2

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	25.3
	25.3
	 
	 
	25.3
	25.3
	 
	430.9
	217.3

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	60.0
	60.0
	 
	 
	60.0
	60.0
	 
	1,020.0
	514.3

	35.0
	35.0
	 
	 
	35.0
	35.0
	 
	595.0
	300.0

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	 
	 
	 
	 
	 
	 
	 
	
	 

	
	
	
	
	
	
	
	
	

	966.0
	966.0
	
	
	966.0
	154.1
	
	11,401.5
	5,537.8

	966.0
	966.0
	
	
	966.0
	154.1
	
	11,401.5
	5,537.8

	985.3
	985.3
	
	
	985.3
	157.2
	
	11,629.5
	5,648.5

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	2019
	2020
	2021
	2022
	2023
	2024
	2025
	
	2026

	2,870.6
	2,802.7
	135.8
	135.8
	2,870.6
	2,601.5
	203.7
	78,976.2
	39,710.8

	 
	 
	 
	 
	 
	 
	 
	 
	 

	
	
	
	
	
	
	
	
	

	2,870.6
	2,802.7
	135.8
	135.8
	2,870.6
	2,601.5
	203.7
	78,976.2
	39,710.8

	
	
	
	
	
	
	
	
	


	
	 
	
	
	
	
	
	
	
	
	
	

	
	
	Gas Turbine Scheduled Maintenance Data Input
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	 
	 
	 
	
	 
	
	
	
	

	
	Gas Turbine Manufactory
	[image: image5.png]1.150
1.100
1.050
1.000
0850
0800
0850
0800

CT temp factor - Data Approximates GE TEA

300 350 400 450 500 550 600 650 700 750 800 850
Temperature - degF




[image: image6.png]



	 
	Year Of COD
	1996
	[image: image7.png]


[image: image8.png]


[image: image9.png]


[image: image10.png]




	

	
	
	
	 
	
	
	
	
	 
	
	

	
	Select GT model/database
	
	
	Estimate Period (years)
	30
	 
	 
	
	

	
	
	
	
	 
	
	
	
	
	
	

	
	Number of Units
	[image: image11.png]


[image: image12.png]



2 

	
	
	Discount for New Parts
	 
	0.0%
	
	
	
	

	
	Intervals Base On
	 
	
	
	Freight for New Parts
	 
	2.0%
	
	 
	 
	 

	
	
	 
	
	
	 
	
	 
	
	
	 
	 

	
	Local Labor Factor
	100.0%
	[image: image13.png]


[image: image14.wmf]GT MASTER 10.0.1 Enron User

188 06-11-2001 16:59:11  file=C:\Tflow4\MYFILES\BNY30F200M.gtm

Net Power 299796 kW

LHV Heat Rate 7427  BTU/kWh

p[psia], T[F], m[kpph], Steam Properties: Thermoflow - STQUIK

1X KWU V84.2

 2 X GT

 115478 kW

 14.65 p

 30 T

 90 %RH

 2643.7 m

 96 ft elev.

 14.51 p

 30 T

 2643.7 m

CH4 51.74 m

 77 T

LHV 1113273 kBTU/h

 365 p

 573 T

 95.02 m

 156.6 p

 578 T

 152.7 p

 2075 T

 2762.6 m

 15.03 p

 993 T

 5525 M

 71.94 %N2+Ar

 12.62 %O2

 3.255 %CO2+SO2

 12.19 %H2O

 990 T

 5525 M

 990 

 865 

 865 

 545 

 510 

 505 

 439 

 369 

 318 

 282 

 233 T

 5525 M

 74385 kW

 2 X ST @

FW

 0.5057 p

 80 T

 541 M

 80 T

 33.3 p

 186 T

 867.9 M

LTE 

 105 T

 867.9 M

 186 T

 33.3 p

 256 T

 54.47 M

 33.3 p

 256 T

 54.47 M

LPB 

 54.47 M

 879.1 M

 132.1 p

 337 T

 879.1 M

IPE2

 132.1 p

 349 T

 114.8 M

IPB 

 126.1 p

 469 T

 103.5 M

IPS1

 11.13 M

 901.1 p

 464 T

 715.9 M

HPE2

 899.9 p

 525 T

 715.9 M

HPE3

 899.9 p

 532 T

 708.8 M

HPB1

 863.9 p

 924 T

 708.8 M

HPS3

 834.4 p

 920 T

 554.2 M

 863.9 p 924 T

 47.3 M

 561.5 p 479 T 200 M

V2

 45.34 M

 308 p

 676 T

 89.2 M

 77.46 M

 116.9 p 465 T

 114.7 p 346 T 28 M

V4

 1.954 M


	
	Discount for Parts Repair
	 
	0.0%
	[image: image15.wmf]GT MASTER 10.0.1 Enron User

188 06-19-2001 15:02:11  file=C:\Tflow4\MYFILES\BNY30F780MNoDB.gtm

Net Power 218280 kW

LHV Heat Rate 9691  BTU/kWh

p[psia], T[F], m[kpph], Steam Properties: Thermoflow - STQUIK

1X KWU V84.2

 2 X GT

 105740 kW

 14.65 p

 30 T

 90 %RH

 2643.7 m

 96 ft elev.

 14.51 p

 30 T

 2643.7 m

CH4 49.16 m

 77 T

LHV 1057717 kBTU/h

 365 p

 573 T

 25 m

 150.7 p

 563 T

 146.9 p

 2075 T

 2690.7 m

 15 p

 988 T

 5381 M

 74.98 %N2+Ar

 13.49 %O2

 3.224 %CO2+SO2

 8.312 %H2O

 985 T

 5381 M

 985 

 860 

 860 

 526 

 490 

 485 

 414 

 331 

 295 

 272 

 233 T

 5381 M

 11036 kW

FW

 0.5057 p

 80 T

 112.7 M

 80 T

 33.3 p

 196 T

 953.8 M

LTE 

 141 T

 953.8 M

 196 T

 33.3 p

 256 T

 32.17 M

 33.3 p

 256 T

 32.17 M

LPB 

 32.17 M

 982.8 M

 75.61 p

 306 T

 982.8 M

IPE2

 75.61 p

 308 T

 125.4 M

IPB 

 66.2 p

 448 T

 96.48 M

IPS1

 28.98 M

 766.2 p

 443 T

 683.6 M

HPE2

 765.1 p

 506 T

 683.6 M

HPE3

 765.1 p

 513 T

 676.8 M

HPB1

 725.8 p

 926 T

 676.8 M

HPS3

 725.3 p

 924 T

 67.55 M

 725.8 p 926 T

 172.5 M

 250 p 415 T 780 M

V2

 170.7 M

 71.92 p

 652 T

 25 M

 70.27 M

 49.56 p 442 T

 43.03 p 315 T 28 M

V4

 1.79 M



	
	 
	 

	
	Price Escalating Factor
	0.0%
	
	
	Freight for Parts Repair
	 
	2.0%
	[image: image16.wmf]GT MASTER 10.0.1 Enron User

188 06-05-2001 10:32:45  file=C:\Tflow4\MYFILES\BNY90F200M.gtm

Net Power 251905 kW

LHV Heat Rate 7669  BTU/kWh

p[psia], T[F], m[kpph], Steam Properties: Thermoflow - STQUIK

1X KWU V84.2

 2 X GT

 94954 kW

 14.65 p

 90 T

 50 %RH

 2350.7 m

 96 ft elev.

 14.5 p

 90 T

 2350.7 m

CH4 44.89 m

 77 T

LHV 965896 kBTU/h

 365 p

 573 T

 95.02 m

 140.5 p

 657 T

 137 p

 2075 T

 2465.7 m

 14.97 p

 1032 T

 4931 M

 70.2 %N2+Ar

 12.39 %O2

 3.137 %CO2+SO2

 14.27 %H2O

 1029 T

 4931 M

 1029 

 887 

 541 

 502 

 497 

 428 

 362 

 312 

 279 

 239 T

 4931 M

 67249 kW

 2 X ST @

FW

 1.411 p

 114 T

 518.1 M

 114 T

 33.3 p

 206 T

 844.5 M

LTE 

 146 T

 844.5 M

 206 T

 33.3 p

 256 T

 45.65 M

 33.3 p

 256 T

 45.65 M

LPB 

 45.65 M

 844.8 M

 125.5 p

 331 T

 844.8 M

IPE2

 125.5 p

 345 T

 96.96 M

IPB 

 119.9 p

 463 T

 96.67 M

IPS1

 0.2037 M

 879.2 p

 455 T

 691.4 M

HPE2

 878.1 p

 519 T

 691.4 M

HPE3

 878.1 p

 529 T

 684.5 M

HPB1

 842.7 p

 959 T

 684.5 M

HPS3

 5.92 M

 814 p

 932 T

 538.2 M

 842.7 p 959 T

 55.5 M

 547.7 p 477 T 200 M

V2

 47.71 M

 298.4 p

 685 T

 89.2 M

 70.53 M

 112.1 p 459 T

 108 p 343 T 28 M

V4

 1.868 M



	
	 
	 

	
	
	 
	 
	 
	 
	
	
	
	
	
	

	
	 
	Interval (EOH)
	 
	Interval (EOS)
	 
	Labor Cost (k$)
	Consumable(K$)
	 
	 
	 
	 

	
	Combustion Inspection
	8,250 
	 
	-
	 
	34 
	33 
	 
	 
	 
	 

	
	HGP Inspection
	33,000 
	 
	-
	 
	1,175 
	150 
	 
	 
	 
	 

	
	Major Inspection
	9,999,999 
	 
	-
	 
	 
	 
	 
	 
	 
	 

	
	
	 
	 
	 
	 
	
	
	 
	
	
	

	
	Name of Parts
	Repair Interval (EOH)
	Replace interval (EOH)
	Repair Interval (EOS)
	Replace Interval (EOS)
	Price of Repair (K$/set)
	Price of Replace (K$/set)
	 
	 # of spare part Sets for rotation
	# of Initial Spare part sets
	Strategic spare  (yes /No)

	
	Row 1 Blade
	33,000 
	66,000 
	-
	-
	94.8
	567.7
	 
	1
	1
	No

	
	Row 2 Blade
	33,000 
	66,000 
	-
	-
	122.0
	734.7
	 
	1
	1
	No

	
	Row 3 Blade
	66,000 
	99,000 
	-
	-
	75.1
	614.6
	 
	1
	0
	No

	
	Row 4 Blade
	-
	99,000 
	-
	-
	0.0
	660.4
	 
	0
	0
	No

	
	Row 1 Vane
	33,000 
	66,000 
	-
	-
	163.7
	828.5
	 
	1
	1
	No

	
	Row 2 Vane
	33,000 
	66,000 
	-
	-
	214.3
	624.4
	 
	1
	1
	No

	
	Row 3 Vane
	33,000 
	99,000 
	-
	-
	70.7
	722.4
	 
	1
	0
	No

	
	Row 4 Vane
	-
	99,000 
	-
	-
	0.0
	871.9
	 
	0
	0
	No

	
	Dampening Rings
	-
	33,000 
	-
	-
	0.0
	20.7
	 
	0
	0
	No

	
	Mixing Elbows
	33,000 
	66,000 
	-
	-
	146.5
	525.3
	 
	1
	0
	No

	
	Seal Rings
	-
	33,000 
	-
	-
	0.0
	103.2
	 
	0
	0
	No

	
	Transition Rings
	-
	33,000 
	-
	-
	0.0
	29.4
	 
	0
	0
	No

	
	Tiles & Hardware
	-
	33,000 
	-
	-
	0.0
	34.6
	 
	0
	0
	No

	
	Compressor Blades
	33,000 
	-
	-
	-
	20.8
	0.0
	 
	0
	0
	No

	
	Compressor Vanes
	33,000 
	-
	-
	-
	13.0
	0.0
	 
	0
	0
	No

	
	Mixing Elbow Hardware
	-
	33,000 
	-
	-
	0.0
	35.3
	 
	0
	0
	No

	
	Inner Casing Hardware
	-
	33,000 
	-
	-
	0.0
	14.4
	 
	0
	0
	No

	
	Miscellaneous Hardware
	-
	33,000 
	-
	-
	0.0
	55.0
	 
	0
	0
	No

	
	Locking Plate Hardware
	-
	33,000 
	-
	-
	0.0
	54.1
	 
	0
	0
	No

	
	Casing Inspection
	33,000 
	-
	-
	-
	25.3
	0.0
	 
	0
	0
	No

	
	Inner Casing
	-
	-
	-
	-
	101.5
	1964.7
	 
	0
	0
	No

	
	Casing Upgrade (old to new)
	-
	-
	-
	-
	0.0
	783.8
	 
	0
	0
	No

	
	 
	-
	-
	-
	-
	0.0
	0.0
	 
	0
	0
	No

	
	 
	-
	-
	-
	-
	0.0
	0.0
	 
	0
	0
	No

	
	Generator field
	33,000 
	-
	-
	-
	60.0
	0.0
	 
	0
	0
	No

	
	Generator stator
	33,000 
	-
	-
	-
	35.0
	0.0
	 
	0
	0
	 

	
	Consumable for Minor
	-
	8,250 
	-
	-
	0.0
	33.3
	 
	0
	0
	 

	
	Consumable for HGPI
	-
	33,000 
	-
	-
	0.0
	183.3
	 
	0
	0
	 

	
	Consumable for Major
	-
	9,999,999 
	-
	-
	 
	 
	 
	0
	0
	 

	
	end
	 
	 
	 
	 
	 
	 
	 
	0
	0
	 

	
	 
	 
	 
	 
	 
	 
	 
	 
	0
	0
	 

	
	 
	 
	 
	 
	 
	 
	 
	 
	0
	0
	 

	
	end
	 
	 
	 
	 
	 
	 
	 
	0
	0
	 


ATTACHMENT

D

MAJOR MAINTENANCE

HISTORY TIMELINE

MAJOR MAINTENANCE HISTORY TIMELINE

· November 1996 – Commercial Operation begins

· April 1998 – HRSG #1 and #2, Repair of lower header feedwater heater tube welds

· October 1998 – CTG #2 major inspection/refurbishment

· March 1999 – Boiler economizer tube failure began (#1 boiler, section #7 of HP economizer )

· April 1999 – CTG#1 major inspection/refurbishment

· December 1999 and January 2000 – Experienced several forced outages due to boiler tube leaks. Since the boiler water supply pH was raised above 9.0 in January, 2000, there have been no further boiler tube leaks resulting in a forced outage.

· June, 2000 – STG #1 Coupling realigned due to high vibration caused by misalignment.

· November, 2000 – Plant forced outage due to ConEd dispatch problem.

· June, 2001 – Water treatment plant achieving final commissioning

ATTACHMENT

E

ENVIRONMENTAL

DUE DILIGENCE

[image: image17.wmf]GT MASTER 10.0.1 Enron User

188 06-05-2001 10:13:15  file=C:\Tflow4\MYFILES\BNY90F550M.gtm

Net Power 215558 kW

LHV Heat Rate 8962  BTU/kWh

p[psia], T[F], m[kpph], Steam Properties: Thermoflow - STQUIK

1X KWU V84.2

 2 X GT

 94968 kW

 14.65 p

 90 T

 50 %RH

 2350.7 m

 96 ft elev.

 14.5 p

 90 T

 2350.7 m

CH4 44.89 m

 77 T

LHV 965896 kBTU/h

 365 p

 573 T

 95.02 m

 140.5 p

 657 T

 137 p

 2075 T

 2465.7 m

 14.96 p

 1032 T

 4931 M

 70.2 %N2+Ar

 12.39 %O2

 3.137 %CO2+SO2

 14.27 %H2O

 1029 T

 4931 M

 1029 

 886 

 527 

 486 

 481 

 409 

 332 

 295 

 272 

 241 T

 4931 M

 30573 kW

 2 X ST @

FW

 0.8553 p

 97 T

 253.2 M

 97 T

 33.3 p

 214 T

 929.1 M

LTE 

 171 T

 929.1 M

 214 T

 33.3 p

 256 T

 31.07 M

 33.3 p

 256 T

 31.07 M

LPB 

 31.07 M

 940.4 M

 80.1 p

 307 T

 940.4 M

IPE2

 80.1 p

 312 T

 109.8 M

IPB 

 70.95 p

 444 T

 98.48 M

IPS1

 11.39 M

 775.6 p

 437 T

 694.8 M

HPE2

 774.5 p

 504 T

 694.8 M

HPE3

 774.5 p

 514 T

 687.9 M

HPB1

 733.5 p

 960 T

 687.9 M

HPS3

 3.208 M

 725.3 p

 932 T

 270.9 M

 733.5 p 960 T

 134.7 M

 476.8 p 462 T 550 M

V2

 129.8 M

 123 p

 635 T

 89.2 M

 72.21 M

 54.87 p 438 T

 46.96 p 317 T 28 M

V4

 1.725 M


Brooklyn Navy Yard Cogeneration Partners, L.P.

Brooklyn, New York

Environmental Site Assessment

June 14, 2001

Prepared By:

Bill Curra, P.E.

Enron Corp.

CONFIDENTIAL

Table of Contents

51Executive Summary


511.0
Introduction


532.0
Site Description


543.0
Adjoining Properties


554.1
Storm Water Management


554.2
Wastewater Management


564.3
Potable Water


564.4
Noise Surveys


564.5
Waste Management


574.6
Spill Prevention and Control


584.7
Air Quality


594.8
Above Ground Storage Tanks (AST)


594.9 
Underground Storage Tanks (UST)


604.10
Oily Water Management


604.11
Surface and Subsurface Contamination


604.13
SARA Title III Reporting


614.14
Risk Management Plan (RMP)/Process Safety Management (PSM)


624.15
Polychlorinated Biphenyl (PCB)


624.16
Herbicides and Pesticides


625.0
Health and Safety Management


626.0
Conclusions


63Reference Reports





Executive Summary

Enron North America (ENA) is considering the acquisition of Mission Energy New York, Inc.’s (MENY) one-half interest in Brooklyn Navy Yard Cogeneration Partners, L.P. (the “Facility”).  As part of the due diligence assessment, an environmental site assessment (ESA) of the Facility was conducted in May and June, 2001 by Enron Corp. Environmental, Health and Safety.  The ESA included a review of environmental records, documents and previously developed reports, a site inspection, and interviews with Facility employees.  Enron had previously commissioned a 3rd party ESA of the asset in January 2000.  This present ESA filled data gaps identified in the previous assessment, and focused on environmental issues, which developed subsequent to the publishing of the earlier ESA report.         

In addition, Facility environmental, health and safety records and permits were reviewed to determine current potential compliance issues.  It does not appear that there are any potential future regulations, which may significantly impact the facility.  It may be necessary to notify the New York State Department of Environmental Conservation of the change of ownership.  

Key findings identified by the present ESA are summarized below:

· There is an unresolved corrective action directive mandated by the New York State Department of Environmental Conservation in connection with an accidental fuel release in April 1997.  A response action addressing the directive, relating to above ground storage tank integrity testing, has been implemented by the Facility; however there has been no concurrence from the agency signaling closure of the case.  This issue is discussed in Section 4.6.

· The Facility Title V Air Permit mandates the use of 0.04% sulfur fuel.  According to the Facility EHS Manager, the availability of this grade of fuel may become limited in the future.  Options to address this include filing for a permit modification to relax the restriction on sulfur content, and/or switching to kerosene as a distillate fuel as discussed in Section 4.7

· The property lease agreement between the current lessor, Brooklyn Navy Yard Development Corporation, and the current lessee, Brooklyn Navy Yard Cogeneration Partners, L.P. was not available for review as of the date of this report.  It was unclear whether Enron will assume the existing lease agreement, or initiate a new agreement.  In either case, the contractual issue of “site restoration” should be given due consideration as discussed in Section 4.11.

Based on the findings of this ESA, Enron Corp. Environmental, Health and Safety does not find evidence of activities or lack of necessary activities that would preclude the proposed acquisition from moving forward.  It should be noted that the key findings listed above are a listing of items that were noted during the assessment that will need to be monitored and/or taken into consideration regarding the acquisition.  A cost summary is not included as no single item found exceeded $100,000 to correct nor does the total for all items exceed $1,000,000 to correct.

1.0
Introduction

Enron North America (ENA) is considering the acquisition of Mission Energy New York, Inc.’s (MENY) one-half interest in Brooklyn Navy Yard Cogeneration Partners, L.P. (consisting of Facility assets and ongoing contracts including power and steam purchase agreements).  The Facility consists of steam and power generating equipment in Building 41 as well as natural gas compression equipment and a boiler feed water treatment plant in two separate structures located to the west of Building 41.  The property and buildings associated with the Facility are leased from Brooklyn Navy Yard Development Corporation (BNYDC).  This ESA evaluates the Facility’s operations and material assets to identify environmental issues, which may pose technical and/or regulatory liabilities.  Of particular interest are liabilities, which could negatively impact the economic analysis of the acquisition, or, which could constitute a fatal flaw for the project.    

In early 2000, ENA, acting as Enron Capital and Trade Resources Corporation, evaluated the acquisition of York Research Corporation’s one-half interest in the cogeneration facility.  At that time, an ESA was conducted by Pilko & Associates, Inc.  This present ESA fills data gaps identified in the previous Pilko ESA, and provides updated information based on developments that have occurred since the January 2000 publication of the Pilko ESA report (Pilko report).  

This report highlights the significant environmental findings identified in the ESA.  The ESA included interviews with Facility employees, a site inspection (conducted on 5/24/01) and review of Facility records and previously-generated environmental reports, including the Pilko report.  Environmental issues which were sufficiently covered in the Pilko report, and which do not constitute fatal flaws or potentially significant impacts to the economic analysis (as discussed above) are summarized simply by referring to the appropriate section of the Pilko report.       

Limitations

A variety of information sources such as regulations, industry standards, employee interviews, and guidelines was utilized in performing the environmental review and risk assessment; however, this ESA was not intended to serve as a rigorous environmental compliance audit.  No sampling of any kind, including air, soils, groundwater, surface water, or building materials was performed as part of this ESA.  In addition, the asset purchase agreement was not available for review at the time of this report.  Also, the property lease agreement with Brooklyn Navy Yard Development Corporation (BNYDC)  was not available for review at the time of this report.  Both of these documents contain provisions, which could influence the environmental condition of the transfer of assets.  Both documents should be evaluated by an environmental professional prior to completing the acquisition.  

2.0
Site Description

The Facility is located at 63 Flushing Avenue, Brooklyn, New York, within the former Brooklyn Navy Yard on approximately 6.8 acres of leased property.  The primary cogeneration facility is located in a brick building identified as Building 41 and includes two parallel independent combined cycle cogeneration trains and associated auxillaries and control systems.  The Facility is under contract to Consolidated Edison (Con Ed) to provide 220 megawatts of electric power and 550,000 pounds of steam per hour in the summer and 800,000 pounds of steam per hour in the winter.  The Facility also provides electricity and steam under contract to BNYDC for use within the industrial park and supplies steam to the City of New York Red Hook Wastewater Treatment Plant.  The Facility is primarily fueled with interruptible natural gas.  Low sulfur diesel fuel is permitted for use in each train for up to 19 days per year.  

To the west of Building 41 are two separate structures one of which is the natural gas compressor building and the other houses the boiler feed water treatment system.

According to Pilko, the existing lease agreement between Brooklyn Navy Yard Cogeneration Partners, L.P. (BNYCPLP) and BYNDC provides easements and right-of-way for items such as the steam and electrical connections to Con Ed and Red Hook, natural gas metering station, and above ground fuel transfer line to Building 41 from the No. 2 dry dock oil receiving facility.  During the winter season, fuel oil is staged on a fuel barge in the dry dock as a ready source of backup fuel.

3.0
Adjoining Properties

Current uses of the adjacent properties are as follows:

North:
The northern portion of Building 41 is not included in the property lease agreement.  The space is unused, and is under the control of BNYDC.  According to Facility EHS Manager Andrew Scano, the space contains unused switching gear, feeder cables, transformers and other surplus equipment.  According to Scano, the space was not included in the Facility-wide asbestos abatement program, and is likely to contain asbestos materials. 

East:
There is a vacant lot on the eastern and southeastern side of the Facility.  The lot, approximately 2 acres in size, is unpaved and is sparsely covered with medium sized hardwood trees.  To the east of the vacant lot is the fenceline marking the BNY property boundary.   

South:
There is a vacant paved parking lot on the southern side of the Facility.  On the date of the ESA site visit, there was a trailer mounted US Filter boiler feed water treatment plant.  The portable plant is staged at the Facility as a contingency against potential unanticipated shutdowns or upsets of the newly commissioned boiler feed water treatment system.

West:
To the west of Building 41 are the natural gas compressor building and the boiler feed water treatment system.  To the northwest, and adjoining Building 41, there is an annex sheet metal building identified as Building 41a, which houses two steam boilers.  The boilers are owned by BNYDC and could be used for contingency generation of steam in the event that the Facility boilers were to become unable to satisfy the steam demand of the BNY. 

The nearest residence is located more than ¼ mile from the Facility and should not be impacted by the activities of the Facility.                                                                         

4.0
Environmental Areas

4.1
Storm Water Management

Two storm water outfalls and once-through cooling water discharge to the East River are addressed by the Facility’s state-issued SPDES permit.  

The cooling water discharge is restricted with regard to its heating effect on the East River and is also restricted to a maximum residual chlorine concentration of 0.2 mg/l.  The permit requires a cooling water minimization study to be completed and submitted on or before 01/01/02 to the New York State Department of Environmental Conservation (NYSDEC).  Also, the SPDES permit states that the Facility shall not be shut down for routine maintenance during the period from December through March in order to protect aquatic biota from severe temperature changes.

The two storm water outfalls that are monitored in accordance with the SPDES permit are: storm water from the sodium hypochlorite delivery truck containment area, and the No. 2 dry dock area which includes the fuel oil storage tank containment area.  Storm water is monitored monthly in accordance with the permit for visible contamination.  Storm water from the sodium hypochlorite area is monitored for flow rate, oil & grease, and total residual chlorine.  Storm water from the No. 2 dry dock area is monitored for flow rate and oil & grease and is tested quarterly for benzene, toluene, ethyl benzene and xylene.  Storm water monitoring reports are submitted monthly, and an summary report is submitted annually to the NYSDEC.      

No records of any notice of violations associated with storm water or cooling water discharges were identified by this ESA.  The Facility appears to be able to meet the terms and conditions of its current SPDES permit without the need for modifications to equipment or operations.  Additional details regarding storm water management are included in Pilko, Section 3.5.2.  

4.2
Wastewater Management

The Facility discharges boiler blowdown, sanitary and utility wastewater streams to the municipal sewer system/Red Hook Wastewater Treatment Plant under a letter notification to the New York City Department of Environmental Protection (NYCDEP).  The NYCDEP has inspected the facility and an industrial wastewater pretreatment permit is pending.  Potential contaminated wastewater streams including seal water, utility water and laboratory sink water are collected in the “dirty” sump.  The contents of the dirty sump are treated through an oil/water separator prior to discharge to the municipal sewer system.  The presence of hydrocarbons in the effluent from the dirty sump is automatically monitored with an inline hydrocarbon detector, which in turn, is coupled to an automatic shut off valve.  The shut off valve is actuated upon detection of hydrocarbon in concentrations exceeding 45 ppm. 

Steam condensate and boiler water blowdown are discharged through the “clean” sump.  These waste streams are blended with shallow groundwater from the gravity French drain system located below the building floor (shallow groundwater is pumped to prevent flooding because the Facility is located within a 100 year flooodplain).  The clean sump is equipped with heat exchange capability and temperature control to prevent exceedence of the 150º F limitation imposed by the permitted wastewater effluent standards.

The effluent from the boiler feed water treatment plant is also discharged to the municipal sewer system.  This wastewater stream is composed of the residue resulting from the purification of the city-supplied potable water.  

There have been violations of effluent standards from the Facility, including an effluent hydrocarbon excursion from the dirty sump and a temperature excursion from the clean sump.  In both cases, voluntary control measures – installing an inline hydrocarbon detector, and adding additional heat exchange capacity - were implemented to prevent a repeat of the excursions.   

The Facility appears to be able to meet the terms and conditions of its current NYCDEP industrial discharge permit without the need for modification of either equipment or operational procedures.  Additional details regarding wastewater management are included in Pilko, Section 3.5.2.  

4.3
Potable Water

Potable water is supplied to the Facility by the New York City municipal water system.  The potable water must be treated prior to use as boiler water; however, for all other Facility applications, it is suitable for use without treatment.

4.4
Noise Surveys

According to Facility EHS Manager Andrew Scano, a 3rd party dosimetry study was conducted in 1998.  Based on the findings of the dosimetry study, all of the process areas within Building 41 as well as the compressor building have been designated as requiring hearing protection.  An additional dosimetry study is scheduled for the month of June 2001 for the recently commissioned boiler feed water treatment plant.  

Ambient (outdoor) noise was evaluated as part of the 1998 dosimetry study.  There were no noise levels detected in excess of standards established by New York City Ordinance.  According to EHS Manager Andrew Scano, there has never been a noise complaint filed on the Facility by vicinity residents.

Both of the turbines were 100% operational on the date of the Facility inspection; the ambient noise on the exterior of Building 41 was audible at a low level, possibly lower than the ambient background level.    

4.5
Waste Management

The Facility generates one ongoing primary hazardous waste stream – natural gas condensate from the compressor operations.  The waste is characterized as hazardous due to ignitability and benzene content.  The Facility generates approximately 200 gallons of condensate waste every three weeks.  The condensate is tested annually for polychlorinated biphenyl (PCB).  There has been one case of detectable PCB since the Facility initiated operations.  The origin of the PCB was determined to be a compressor station associated with the natural gas supply pipeline located upstream of the Facility.   

The Facility’s annual hazardous waste summary report for 2000 identifies the Facility as a Large Quantity Generator, which shipped offsite three hazardous waste streams: 7.9 tons of waste natural gas condensate, 0.1 tons of spills debris (ie, condensate-soaked rags, which were hazardous due to benzene content), and 0.5 tons of waste paint-related waste.

Non-hazardous wastes are also generated at the Facility and are shipped offsite for disposal.  Non-hazardous wastes include used oil, rags and absorbent pads, spent activated carbon, antifreeze and general plant trash and debris.  

There were no unresolved waste management issues identified by this ESA.  Additional details regarding hazardous and non-hazardous waste management are included in Pilko, Section 3.5.3.  

4.6
Spill Prevention and Control

The Facility has extensive contingency plans and facility response plans which address the prevention of spills and releases and provide reporting and response procedures in the event of an incident.  These plans respond to regulatory mandates of the USEPA, NYSDEC, NYCDEP, US Coast Guard and NYC Fire Department.  The contingency plans comprise much of the core curriculum for environmental training of Facility personnel.      

The Facility handles No. 2 fuel oil, aqueous ammonia solution, sodium hypochlorite solution, water treatment chemicals and drum and tote containers of oils, lubricants, and other chemicals.  All of the spill prevention and control measures mandated by the jurisdictional agencies listed above have been implemented including secondary containment of bulk storage containers, and double-walled, above ground piping for transport of fuel oil from the dry dock area into the plant.  

In April 1997, the Facility experienced an overflow release from the fuel oil day storage tank.  The release was due to a malfunction in the level control instrumentation.  The released fuel oil was contained on the pavement, and all required emergency notifications were made.  Improvements were made to the level control system as requested by the NYSDEC and the NYC Fire Department to include adding redundant level control  protection in the day tank.  In addition, the 350,000 gal fuel storage tank was improved by adding level detection in the secondary containment, and adding a manual fuel oil cutoff switch, which can be monitored and activated from the control room.  In addition, the Facility has initiated a program for 3rd party inspection and integrity assessment for the 350,000 gal tank on a 10 year frequency.     

The NYC Fire Department approved the response actions implemented by the Facility, and closed the case.

The NYSDEC requested conductivity testing of the 350,000 gal tank components to assess the potential for corrosion, as well as permeability testing of the floor of the concrete secondary containment.  The Facility performed the tests using a 3rd party tank testing firm.  The test reports were provided to NYSDEC Bureau of Spills Prevention and Control; however to date, no response has been received indicating that the case has been officially closed.              

The Facility retains the on-call services of an emergency response contractor for responding to hazardous substance spills or releases.  A contractor is required to be capable of responding to emergencies within two hours of notification.

With the exception of the No. 2 fuel oil release described above, there were no unresolved spill prevention and control issues identified by this ESA.  Additional details regarding spill prevention and control are included in Pilko, Section 3.5.4.  

4.7
Air Quality

The NYSDEC  has issued the Facility a Title V air permit no. 2-6101-00185/00008, effective 12/5/2000, with an expiration date of 12/4/2005.  The 124-page air permit is posted on the NYSDEC website at the following URL address:

    http://www.dec.state.ny.us/website/dar/boss/afs/permits/261010018500008.pdf

The primary source of air emissions at the Facility is the natural gas-fired cogeneration system.  The Facility design incorporates Best Available Control Technology such as low NOx burners, selective catalytic reduction of NOx using ammonia injection, and catalytic oxidation of CO to CO2.  Facility emissions are monitored using a continuous emission monitoring system.  The turbines are authorized to burn bio-gas from the Red Hook Waste Water Treatment Plant in conjunction with natural gas.  The gas turbines are also allowed to burn distillate oil (defined as #1 or #2 fuel oil, kerosene or Jet A fuel) for a maximum of 1008 hours per year with no more than 96 hours during the period of May 1st through October 31st of each year.  

In addition to the cogeneration system, the Facility has two diesel fired emergency generators mounted on the roof of Building 41.

Stack testing of the turbines and emergency generators was conducted in September 1996 as part of the PSD Permit to Construct and as a requirement of the Certificate to Operate.  The testing was conducted by an independent 3rd party contractor.  The turbines were tested using natural gas, as well as No. 2 fuel oil, and the emergency generators were fired on No. 2 fuel oil.  All pollutants were below the maximum allowable air permit emissions limitations.    

The Title V permit mandates the use of low sulfur fuel - 0.04% by weight -  when operating using distillate fuel.  The 0.04% sulfur limitation resulted from ambient air modeling conducted by a 3rd party air permitting consulting firm hired by the Facility to develop the Title V permit application.  According to Andrew Scano, Facility EHS Manager, the ambient air modeling incorporated meterological data collected from a near vicinity meterological station during the unrepresentatively hot and windless calendar year 1980.  The model also based its exposure assessment on hypothetical “flagpole receptors” positioned at the top of a nearby downwind building.  According to Scano, the exposure point is not a valid modeling objective because the upper portion of the target building is uninhabitable.  A more realistic and representative exposure analysis would consider exposures at areas, which are currently (or in the future projected to be) occupied by residents or workers.  Although these criteria have not yet been modeled, Scano contends that the use of alternative exposure points and more recent meterological data would result in a higher sulfur allowance.  According to Scano, the Facility intends to update the ambient model using the services of a independent contractor.  Based on the outcome of the modeling, the Facility intends to file for a more permissive sulfur content for the distillate fuel.  Andrew Scano estimated that the processing time of the permit modification would be between 6 months and 1.5 years.  He would not comment on the likelihood of agency approval of the modification.  

The distillate fuel sulfur content restriction may become significant because, according to Scano, the regional supplier of low sulfur diesel fuel may discontinue distribution operations at some point in the future.  As an alternative to diesel fuel, kerosene is permitted to be fired.  Kerosene is typically lower in sulfur than diesel fuel by as much as two orders of magnitude, and consequently, the reduction in SOx emissions would yield marketable SOx credits for the Facility.  According to Scano, SOx  credits are currently valued at approximately $180/ton.          

With the exception of the sulfur issue described above, the Facility appears to be able to meet the terms and conditions of its current Title V air permit without the need for modification of either equipment or operational procedures. There were no unresolved air quality issues or notice of violations identified by this ESA.  Additional details regarding air quality at the Facility are included in Pilko, Section 3.5.1.  

4.8
Above Ground Storage Tanks (AST)

The Facility has the following ASTs:

Volume (gal)
Substance


350,000
Distillate fuel oil

1,000
Fire suppression foam

5,400
Aqueous ammonia

60,000
Fire water storage

1,000 
Distillate fuel oil, day tank

The following tanks are located inside of buildings:

Volume (gal)
Substance


1,000
Water treatment chemical

1,000
Water treatment chemical

400 Sodium hypochlorite solution

275
Gas distillate

250
Lubrication oil storage tank



As described in Section 4.6, above, the 350,000 gal fuel oil tank is pending concurrence and approval from NYSDEC for response actions relating to the 1997 fuel oil release.  Otherwise, the Facility ASTs are permitted by, and satisfy the integrity, labeling, inspections, monitoring and reporting requirements of NYDEC.  

4.9 
Underground Storage Tanks (UST)

There are no USTs associated with the facility.

4.10
Oily Water Management

Oily water is collected via drain systems from the various processes within the facilities and is routed to the “dirty” sump for pretreatment prior to discharging to the municipal sewer system.  Phase separated oil is separated from the wastewater by use of a wier and skimmer system.  Skimmed oil is picked up monthly for offsite management by a 3rd party waste oil marketer.  The wastewater underflow is monitored for hydrocarbons with a VOC meter.  In addition, the wastewater discharge from the Facility is sampled and tested quarterly for oil related parameters including heavy metals and total petroleum hydrocarbons.  

There were no unresolved oily water management issues identified by this ESA.  

4.11
Surface and Subsurface Contamination

A Phase II environmental audit was conducted by Blasland & Bouck Engineers, P.C. in July 1992 in advance of the construction of the improvements to the Facility.  The investigation identified the presence of volatile organic contaminants, semi-volatile organics and metals in the subsurface soil and or/groundwater.  The report was reviewed by the NYSDEC; no additional corrective action was directed.  

There was no evidence of recent releases (ie, subsequent to the 1992 environmental audit) of contaminants to the subsurface noted during the site inspection on May 24, 2001.  

The concern for surface and subsurface contamination on leased real estate relates to the lease agreement.  Lease agreements typically include terms and conditions for restoration of the property to “pre-lease” conditions upon termination of the lease agreement.  If that is the case, there should be a “baseline” description of the pre-lease property condition.  It is possible that the 1992 Blasland & Bouck report could suffice for a such a baseline.  The lease agreement for the Facility was not reviewed as part of this ESA.      

4.13
SARA Title III Reporting

The Facility is subject to the reporting requirements of SARA Title III Section 312 Tier Two.  The Tier Two report for reporting year 2000 listed 23 hazardous substances reported.  No. 2 fuel oil was the highest amount of a single reportable substance reported, with electrical insulating oil and lubricating oil the 2nd and 3rd, respectively.   

The Facility is subject to the reporting requirements of SARA Title III Section 313 Toxic Release Inventory (TRI).  The TRI report for reporting year 1999 reflects total on-site releases of ammonia of 41,400 lbs and total on-site releases of chlorine of 1580 lbs.  The TRI report for reporting year 2000 is due to be submitted on June 30; total on-site release quantities of ammonia and chlorine are not anticipated to change significantly from the previous year.

4.14
Risk Management Plan (RMP)/Process Safety Management (PSM)

The Facility is not subject to RMP because it does not store applicable substances in quantities exceeding their reporting thresholds.  

The Facility does not store substances that are covered by the PSM program and therefore the facility does not have to follow PSM.

4.15
Polychlorinated Biphenyl (PCB)

There are no PCB’s associated with the Facility. 

4.16
Herbicides and Pesticides

The Facility does not use herbicides or pesticides on-site.

5.0
Health and Safety Management

The Facility currently has a fulltime EH&S Engineer.  The facility has an active safety training program for the employees which includes 8 hours of OSHA training, 24 hour Hazardous Waste Operator (HAZWOPER) Technician training and an 8 hour HAZWOPER annual refresher.  

There is an extensive CO2 fire suppression system in place for hydrocarbon-related fires.  The CO2 system has been inspected and approved by the New York City Fire Department.  The Facility does not maintain a fire brigade and depends on the New York City Fire Department for fire fighting services.

Safety equipment including eye wash stations and fire extinguishers at the Facility appeared to be well maintained and the overall housekeeping at the Facility appeared to be excellent.  There were no unresolved health and safety issues at the Facility that were identified by this ESA.  

6.0
Findings and Conclusions

Key findings identified by the present ESA are summarized below:

· There is an unresolved corrective action directive mandated by the New York State Department of Environmental Conservation in connection with an accidental fuel release in April 1997.  A response action addressing the directive, relating to above ground storage tank integrity testing, has been implemented by the Facility; however there has been no concurrence from the agency signaling closure of the case.  This issue is discussed in Section 4.6.

· The Facility Title V Air Permit mandates the use of 0.04% sulfur fuel.  According to the Facility EHS Manager, the availability of this grade of fuel may become limited in the future.  Options to address this include filing for a permit modification to relax the restriction on sulfur content, and/or switching to kerosene as a distillate fuel as discussed in Section 4.7

· The property lease agreement between the current lessor, Brooklyn Navy Yard Development Corporation, and the current lessee, Brooklyn Navy Yard Cogeneration Partners, L.P. was not available for review as of the date of this report.  It was unclear whether Enron will assume the existing lease agreement, or initiate a new agreement.  In either case, the contractual issue of “site restoration” should be given due consideration as discussed in Section 4.11.

Reference Reports

ESA of Brooklyn Navy Yard Cogeneration Partners L.P., Pilko & Associates, Inc, January 2000.

Independent Technical Review of the York Research Corporation Electric Generating Asset Portfolio, Stone & Webster management Consultants, Inc. June 1998

ATTACHMENT 1

REFERENCE LIST

1) Independent Technical Review of York Research Corporation InnCOGEN and Big Spring Powerplants – FINAL REPORT for Credit Suisse First Boston Corporation – May 9, 2000 by Stone & Webster Consultants.

2) Independent Technical Review of the York Research Corporation Electric Generating Asset Portfolio for Credit Suisse First Boston Corporation – June 30, 1998 by Stone & Webster Management Consultants, Inc. Project Finance Services Division.

3) ESA of Brooklyn Navy Yard Cogeneration Partners L.P., Pilko & Associates, Inc, January 2000.

ATTACHMENT

F

DIRECTIONS TO 

BROOKLYN NAVY YARD
Brooklyn Navy Yard

BNY CoGen is located on an approximately 6.8-acre site in the Brooklyn Navy Yard in Brooklyn, New York.  The site is at the edge of a ship basin off the East River and is leased from the BNYDC.  The Project is located in an existing building, B-41, of the Brooklyn Navy Yard.  The Brooklyn Navy Yard is a 261-acre facility, containing 4.3 million square feet of building space, located on the Brooklyn shoreline between the Manhattan and Williamsburg bridges.

The power plant facility is located at 63 Flushing Avenue, Brooklyn, New York, within the former Brooklyn Navy Yard on approximately 6.8 acres of leased property.  The primary cogeneration facility is located in a brick building identified as Building 41.

ATTACHMENT

 G

PERFORMANCE   DATA

	BROOKLYN NAVY YARD

	EXPECTED PERFORMANCE SUMMARY

	 
	
	
	
	
	
	
	 

	AMBIENT
	GTG
	STEAM
	CON ED
	LP
	NET PLANT
	NET PLANT
	NET PLANT

	TEMP.
	UNITS
	TURBINES
	STEAM
	STEAM
	HEAT RATE
	POWER
	HEAT RATE

	(Deg. F)
	OPERATING
	OPERATING
	SALES (Kpph)
	SALES
	Btu/Kwh (HHV)
	(KW)
	Btu/Kwh (LHV)

	 
	 
	 
	 
	 
	 
	 
	 

	30
	2
	2
	200
	28
	8,241
	299,796
	7,427

	 
	
	 
	
	 
	
	 
	 

	90
	2
	2
	200
	28
	8,510
	251,905
	7,669

	 
	
	 
	
	 
	
	 
	 

	90
	2
	2
	550
	28
	9,944
	215,558
	8,962

	 
	
	 
	
	 
	
	 
	 

	90
	2*
	2
	200
	28
	8,564
	270,776
	7,718

	
	
	
	
	
	
	
	

	90
	2*
	2
	550
	28
	9,894
	234,363
	8,917

	
	
	
	
	
	
	
	

	30
	2
	1
	780
	28
	10,753
	218,280
	9,691

	
	
	
	
	
	
	
	

	59
	2
	1
	750
	23
	11,105
	197,692
	10,008

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	 
	 
	 
	 
	 
	 
	 
	 

	* Performance with a 1925 ton chiller added to gas turbine inlet.


[image: image18.wmf]GT MASTER 10.0.1 Enron User

188 06-05-2001 15:43:34  file=C:\Tflow4\MYFILES\BNY90FCH200M.gtm

Net Power 270776 kW

LHV Heat Rate 7718  BTU/kWh

p[psia], T[F], m[kpph], Steam Properties: Thermoflow - STQUIK

1X KWU V84.2

 2 X GT

 105628 kW

 14.65 p

 90 T

 50 %RH

 2524.2 m

 96 ft elev.

 14.5 p

 59 T

 2512.8 m

CH4 48.56 m

 77 T

LHV 1044911 kBTU/h

 365 p

 573 T

 95.02 m

 50 p

 281 T

 40.25 m

 149.5 p

 620 T

 145.8 p

 2075 T

 2629.8 m

 15 p

 1010 T

 5260 M

 70.94 %N2+Ar

 12.47 %O2

 3.193 %CO2+SO2

 13.39 %H2O

 1007 T

 5260 M

 1007 

 875 

 544 

 505 

 499 

 430 

 355 

 309 

 278 

 241 T

 5260 M

 64967 kW

 2 X ST @

FW

 1.289 p

 110 T

 471.4 M

 110 T

 33.3 p

 208 T

 878.7 M

LTE 

 151 T

 878.8 M

 208 T

 33.3 p

 256 T

 45.31 M

 33.3 p

 256 T

 45.31 M

LPB 

 45.31 M

 879.3 M

 109.9 p

 326 T

 879.3 M

IPE2

 109.9 p

 335 T

 115.4 M

IPB 

 101.1 p

 458 T

 114.8 M

IPS1

 0.3179 M

 892.2 p

 457 T

 707.1 M

HPE2

 891.1 p

 522 T

 707.1 M

HPE3

 891.1 p

 531 T

 700.1 M

HPB1

 855.1 p

 939 T

 700.1 M

HPS3

 1.019 M

 825.8 p

 932 T

 547.2 M

 855.1 p 939 T

 55.67 M

 555.8 p 478 T 200 M

V2

 46.08 M

 299.2 p

 682 T

 89.2 M

 14.82 M

 101 p 456 T

 65.69 p 340 T 28 M

V4

 6.17 M

 50 

 281 

 80.5 


[image: image19.wmf]GT MASTER 10.0.1 Enron User

188 06-05-2001 15:24:27  file=C:\Tflow4\MYFILES\BNY90FCH550M.gtm

Net Power 234363 kW

LHV Heat Rate 8917  BTU/kWh

p[psia], T[F], m[kpph], Steam Properties: Thermoflow - STQUIK

1X KWU V84.2

 2 X GT

 105649 kW

 14.65 p

 90 T

 50 %RH

 2524.2 m

 96 ft elev.

 14.5 p

 59 T

 2512.8 m

CH4 48.56 m

 77 T

LHV 1044911 kBTU/h

 365 p

 573 T

 95.02 m

 29.72 p

 281 T

 40.17 m

 149.5 p

 620 T

 145.8 p

 2075 T

 2629.8 m

 15 p

 1010 T

 5260 M

 70.94 %N2+Ar

 12.47 %O2

 3.193 %CO2+SO2

 13.39 %H2O

 1007 T

 5260 M

 1007 

 874 

 528 

 488 

 481 

 408 

 321 

 290 

 270 

 242 T

 5260 M

 28195 kW

 2 X ST @

FW

 0.7806 p

 94 T

 208.5 M

 94 T

 33.3 p

 216 T

 965.1 M

LTE 

 176 T

 965.1 M

 216 T

 33.3 p

 256 T

 27.84 M

 33.3 p

 256 T

 27.84 M

LPB 

 27.84 M

 979.2 M

 66.14 p

 299 T

 979.2 M

IPE2

 63.45 p

 296 T

 132.6 M

IPB 

 45.72 p

 436 T

 118.6 M

IPS1

 14.14 M

 777.6 p

 436 T

 711.5 M

HPE2

 776.4 p

 506 T

 711.5 M

HPE3

 776.4 p

 515 T

 704.5 M

HPB1

 734.2 p

 941 T

 704.5 M

HPS3

 0.8491 M

 725.3 p

 932 T

 280.6 M

 734.2 p 941 T

 133.7 M

 477.2 p 462 T 550 M

V2

 125.2 M

 123.9 p

 630 T

 89.2 M

 17.83 M

 44.35 p 433 T

 29.72 p 309 T 28 M

V4

 6.442 M

 29.72 

 281 

 80.42 


[image: image20.wmf]
[image: image21.wmf]
[image: image22.wmf]GT MASTER 10.0.1 Enron User

188 06-19-2001 15:16:10  file=C:\Tflow4\MYFILES\BNY59F750MNoDB.gtm

Net Power 197692 kW

LHV Heat Rate 10008  BTU/kWh

p[psia], T[F], m[kpph], Steam Properties: Thermoflow - STQUIK

1X KWU V84.2

 2 X GT

 95960 kW

 14.65 p

 59 T

 60 %RH

 2519.1 m

 96 ft elev.

 14.5 p

 59 T

 2519.1 m

CH4 45.97 m

 77 T

LHV 989234 kBTU/h

 250 p

 433 T

 25 m

 143.7 p

 604 T

 140.1 p

 2075 T

 2564.1 m

 14.98 p

 1005 T

 5128 M

 74.58 %N2+Ar

 13.51 %O2

 3.159 %CO2+SO2

 8.743 %H2O

 1002 T

 5128 M

 1002 

 869 

 525 

 488 

 482 

 412 

 335 

 296 

 273 

 243 T

 5128 M

 10119 kW

FW

 0.9108 p

 99 T

 121.1 M

 99 T

 33.3 p

 217 T

 943.1 M

LTE 

 177 T

 943.1 M

 217 T

 33.3 p

 256 T

 32.58 M

 33.3 p

 256 T

 32.58 M

LPB 

 32.58 M

 950.1 M

 83.58 p

 309 T

 950.1 M

IPE2

 83.58 p

 315 T

 111 M

IPB 

 73.86 p

 444 T

 104 M

IPS1

 6.923 M

 765.2 p

 441 T

 671.7 M

HPE2

 764.2 p

 505 T

 671.7 M

HPE3

 764.2 p

 513 T

 665 M

HPB1

 725.7 p

 940 T

 665 M

HPS3

 16.07 M

 0.1943 M

 725.2 p

 932 T

 63.92 M

 725.7 p 940 T

 166.4 M

 250 p 433 T 750 M

V2

 161 M

 71.66 p

 668 T

 25 M

 82.37 M

 53.2 p 437 T

 60.02 p 323 T 23 M

V4

 1.411 M




	
	Dodger 2000 Budget (Palmark's Op. Data)
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	Item #
	Item
	Jan-00
	Feb-00
	Mar-00
	Apr-00
	May-00
	Jun-00
	Jul-00
	Aug-00
	Sep-00
	Oct-00
	Nov-00
	Dec-00
	
	Traceability
	
	
	

	a
	Stm BBtu
	761
	730
	706
	487
	586
	506
	516
	526
	509
	526
	538
	755
	
	Palmark's Op. Data page 8 of 8
	
	

	b
	Fuel BBtu
	1860
	1737
	1737
	1220
	1458
	1569
	1625
	1634
	1544
	1261
	1400
	1845
	
	Palmark's Op. Data page 8 of 8
	
	

	c
	Net Elec 1000 MwH
	163.19
	152.61
	156.78
	112.56
	140.92
	156.35
	162.47
	162.74
	148.97
	119.14
	126.58
	162.35
	
	Palmark's Op. Data page 8 of 8
	
	

	d1
	Parasitic Pwr -MW                (pk)
	5.8
	5.8
	5.8
	6.0
	6.0
	5.8
	5.8
	5.8
	5.8
	6.0
	6.0
	6.2
	
	Palmark's Op. Data page 2 of 8
	
	

	d2
	Parasitic Pwr - MW               (off-pk)
	5.5
	5.5
	5.5
	5.8
	5.8
	5.8
	5.8
	6
	5.8
	5.8
	5.8
	6.2
	
	Palmark's Op. Data page 2 of 8
	
	

	d3
	Average Parasitic                  Pwr - MW
	5.7
	5.7
	5.7
	5.9
	5.9
	5.8
	5.8
	5.8
	5.8
	5.9
	5.9
	6.2
	
	Weighted Avg From d1,d2 and f
	
	

	e
	Hours
	724
	681
	701
	507
	627
	693
	729
	729
	674
	531
	572
	729
	
	Palmark's Op. Data page 2 of 8
	
	

	f
	On-Pk/Off-Pk Hrs
	1.2839
	1.3646
	1.5399
	0.9351
	2.1400
	1.4401
	1.2781
	1.3980
	1.5434
	0.9667
	0.9195
	1.2781
	
	Palmark's Op. Data page 2 of 8
	
	

	g
	Gross Elec 1000 MWH
	168.9
	158.3
	162.5
	118.5
	146.9
	162.2
	168.3
	168.5
	154.8
	125.0
	132.5
	168.6
	
	Calc: Sum item c + item d3
	
	

	h
	CT Temp Factor
	1.084
	1.078
	1.054
	1.024
	1.000
	0.967
	0.952
	0.955
	0.976
	1.006
	1.039
	1.069
	
	Curve Fit - Est. from GE Fr7EA data
	

	i
	Inlet Temp
	32
	34
	42
	52
	60
	71
	76
	75
	68
	58
	47
	37
	
	Palmark's Op. Data page 1 of 8
	
	

	j
	Avg Net Gen-MWh/Hr
	225.4
	224.1
	223.7
	222.0
	224.8
	225.6
	222.9
	223.2
	221.0
	224.4
	221.3
	222.7
	
	Calc:  item c / item e x 1,000
	
	

	k
	Avg Stm-MMBtu/Hr
	1051.1
	1072.0
	1007.1
	960.6
	934.6
	730.2
	707.8
	721.5
	755.2
	990.6
	940.6
	1035.7
	
	Calc:  item a / item e x 1,000
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	l
	Avg Gross CTG Out-MWh/Hr
	223.1
	221.9
	216.9
	210.8
	205.8
	199.0
	196.0
	196.6
	200.9
	207.1
	213.9
	220.0
	
	Calc:  ISO  CTG Output x .97 x item h
	

	m
	Net CTG Out (less all Sta. Load)
	217.5
	216.2
	211.3
	204.9
	199.9
	193.2
	190.2
	190.8
	195.1
	201.2
	208.0
	213.8
	
	Callc: Gross CTG less Parasitics
	

	n
	Avg STG Out-MWh/Hr
	7.9
	7.9
	12.4
	17.1
	24.9
	32.4
	32.7
	32.5
	25.9
	23.2
	13.3
	8.9
	
	Calc:  item j - item m
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	Calculation for Net Output  assuming maximum usage of HP steam for generation, e.g., minimum steam (200,000 Lbs/Hr) extracted at 350 psi.
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	(all figures are total                                   for two(2) CTG's                                      and two (2) STG's)
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	o1
	Avg HP Stm Avail -                          M#/Hr (pk)
	879.28
	888.13
	846.09
	784.75
	773.11
	615.00
	602.70
	615.00
	630.99
	794.19
	764.50
	879.28
	
	Palmark's Op. Data page 3 of 8
	
	

	o2
	Avg HP Stm Avail -                          M#/Hr (off-pk)
	872.19
	904.79
	849.21
	805.51
	789.10
	627.30
	602.70
	615.00
	653.13
	826.57
	778.46
	861.61
	
	Palmark's Op. Data page 3 of 8
	
	

	p
	Avg HP Stm Avail                                      to C. - M#/Hr
	676.17
	695.17
	647.32
	595.48
	578.20
	420.04
	402.70
	415.00
	439.69
	610.66
	571.77
	671.52
	
	Weighted Avg From o1, o2 and f,less 200
	

	q
	Avg HP Stm Avail                                          to C. - MMBtu/hr
	310.36
	319.09
	297.12
	273.32
	265.39
	192.80
	184.84
	190.49
	201.82
	280.29
	262.44
	308.23
	
	(Hin - Hout) x item p / 1,000
	
	

	r
	Min HP Stm to Extr.                                     - MMBtu/Hr
	21.00
	21.00
	21.00
	21.00
	21.00
	21.00
	21.00
	21.00
	21.00
	21.00
	21.00
	21.00
	
	(Hin - Hout) x 200 / 1,000
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	s
	MWH at STG for eff=.97
	94.2
	96.7
	90.4
	83.6
	81.4
	60.8
	58.5
	60.1
	63.3
	85.6
	80.6
	93.6
	
	Calc: .97 x (item q + item r) / 3.413
	

	t
	New CCCT Out - MW
	311.6
	312.9
	301.7
	288.5
	281.3
	254.0
	248.7
	250.9
	258.4
	286.8
	288.5
	307.4
	
	Calc:item m+ item s (revised12.18.00)
	

	u
	Net HR - Btu/kW - HHV
	8244
	8152
	8214
	8340
	8267
	8913
	8965
	8934
	8865
	8280
	8483
	8233
	
	Calc:[(item b / item e) / item t)]x1,000,000

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	CT inlet temp
	30.0
	35.0
	40.0
	45.0
	50.0
	55.0
	60.0
	65.0
	70.0
	75.0
	80.0
	85.0
	
	
	
	
	
	

	
	CT temp factor
	1.103
	1.086
	1.069
	1.051
	1.034
	1.017
	1.000
	0.983
	0.966
	0.949
	0.931
	0.914
	
	
	
	
	
	

	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	1.120
	230.5
	319.8
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	note: at 20 degF inlet air temp, based on the above evaluation, the net MWh/hr output is expected to be about 320.
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	Projected Steam Use for yr 2000 from Palmark Data: (in 1000 lbs)
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	Jan-00
	Feb-00
	Mar-00
	Apr-00
	May-00
	Jun-00
	Jul-00
	Aug-00
	Sep-00
	Oct-00
	Nov-00
	Dec-00
	
	
	
	
	
	

	
	Con-Ed Steam (350 psi)
	633634
	611026
	594241
	408395
	494768
	431014
	439368
	448335
	433850
	438910
	445278
	632476
	
	6011295
	
	
	
	

	
	BNYDC Steam (120 psi)
	32990
	26222
	19094
	6084
	4389
	0
	0
	0
	0
	9027
	12870
	24390
	
	135066
	
	
	
	

	
	Red Hook Steam (120 psi)
	17540
	16703
	15711
	7605
	9405
	10395
	12371
	12511
	11546
	7965
	8580
	16121
	
	146453
	
	
	
	


�EMBED Word.Picture.8���



























































































































































































































































Panther Creek Power Plant

Technical & Operational Due Diligence

PAGE  
1
Project Battleship

Technical & Operational Due Diligence


_980940508.doc



