[image: image1.png]i Rolls-Royce





[image: image1.png]

COBERRA 6562 DLE

Gas Turbine Site Performance

CASE 1: 
5700 Ft. ASL

Point Number
1
2
3
4
5

Ambient Temperature (°F)
59
68
77
86
95

Elevation (ft ASL)
5700
5700
5700
5700
5700

Relative Humidity (%)
60
60
60
60
60

Combustor
DLE
DLE
DLE
DLE
DLE

Fuel
Nat Gas
Nat Gas
Nat Gas
Nat Gas
Nat Gas

Lower Heating Value (Btu/lb)
21114
21114
21114
21114
21114

Inlet Loss (in H2O)
2.5
2.5
2.5
2.5
2.5

Exhaust Loss (in H2O)
4
4
4
4
4

Shaft Power (HP)
30271*
28942
27635
26343
25073

Heat Rate (BTU/HP.Hr)
6904**
6986
7077
7179
7294

PT Speed (RPM)
4800
4800
4800
4800
4800

Fuel Flow (lb/Hr)
9899
9575
9262
8957
8662

PT Exit Flow (lb/s)
162.5
157.8
153
148.3
143.4

NOx (vppm)
25
25
25
25
25

NOx (tons/yr)
102
99
96
93
90

CO (vppm)
5
5
5
5
5

CO (tons/yr)
12
12
12
11
11

Guarantee Tolerances:

*Output Power (HP)

0%

**Fuel Rate (BTU/HP-Hr)

+3%

Guarantees are based on a clean and new engine.  All other data is expected, not guaranteed. 

Note:    

1)
Tons/yr based upon 8760 hours per year and 1 ton = 2000 lb.

COBERRA 6562 DLE

Gas Turbine Site Performance

CASE 2: 
6000 Ft. ASL


1
2
3
4
5

Ambient Temperature (°F)
59
68
77
86
95

Elevation (ft ASL)
6000
6000
6000
6000
6000

Relative Humidity (%)
60
60
60
60
60

Combustor
DLE
DLE
DLE
DLE
DLE

Fuel
Nat Gas
Nat Gas
Nat Gas
Nat Gas
Nat Gas

Lower Heating Value (Btu/lb)
21114
21114
21114
21114
21114

Inlet Loss (in H2O)
2.5
2.5
2.5
2.5
2.5

Exhaust Loss (in H2O)
4
4
4
4
4

Shaft Power (HP)
29930*
28614
27326
26049
24811

Heat Rate (BTU/HP.Hr)
6905**
6986
7077
7180
7293

Fuel Flow (lb/Hr)
9788
9467
9159
8858
8571

PT Exit Flow (lb/s)
160.7
156
151.3
146.6
141.9

NOx (vppm)
25
25
25
25
25

NOx (tons/yr)
100
98
95
92
89

CO (vppm)
5
5
5
5
5

CO (tons/yr)
12
12
12
11
11

Guarantee Tolerances:

*Output Power (HP)

0%

**Fuel Rate (BTU/HP-Hr)

+3%

Guarantees are based on a clean and new engine.  All other data is expected, not guaranteed. 

Note:    

1) Tons/yr based upon 8760 hours per year and 1 ton = 2000 lb.

COBERRA 6562 DLE

Gas Turbine Site Performance

CASE 3 : 
6800 Ft. ASL


1
2
3
4
5

Ambient Temperature (°F)
59
68
77
86
95

Elevation (ft ASL)
6800
6800
6800
6800
6800

Relative Humidity (%)
60
60
60
60
60

Combustor
DLE
DLE
DLE
DLE
DLE

Fuel
Nat Gas
Nat Gas
Nat Gas
Nat Gas
Nat Gas

Lower Heating Value (Btu/lb)
21114
21114
21114
21114
21114

Inlet Loss (in H2O)
2.5
2.5
2.5
2.5
2.5

Exhaust Loss (in H2O)
4
4
4
4
4

Shaft Power (HP)
29034*
27775
26509
25286
24095

Heat Rate (BTU/HP.Hr)
6906**
6986
7078
7180
7294

Fuel Flow (lb/Hr)
9496
9190
8886
8599
8324

PT Exit Flow (lb/s)
155.9
151.4
146.8
142.2
137.7

NOx (vppm)
25
25
25
25
25

NOx (tons/yr)
97
95
92
89
86

CO (vppm)
5
5
5
5
5

CO (tons/yr)
12
12
11
11
10

Guarantee Tolerances:

*Output Power (HP)

0%

**Fuel Rate (BTU/HP-Hr)

+3%

Guarantees are based on a clean and new engine.  All other data is expected, not guaranteed. 

Note:    

1)
Tons/yr based upon 8760 hours per year and 1 ton = 2000 lb.
COBERRA 6562 DLE

Gas Turbine Site Performance

CASE 4: 
7400 Ft. ASL


1
2
3
4
5

Ambient Temperature (°F)
59
68
77
86
95

Elevation (ft ASL)
7400
7400
7400
7400
7400

Relative Humidity (%)
60
60
60
60
60

Combustor
DLE
DLE
DLE
DLE
DLE

Fuel
Nat Gas
Nat Gas
Nat Gas
Nat Gas
Nat Gas

Lower Heating Value (Btu/lb)
21114
21114
21114
21114
21114

Inlet Loss (in H2O)
2.5
2.5
2.5
2.5
2.5

Exhaust Loss (in H2O)
4
4
4
4
4

Shaft Power (HP)
28386*
27155
25926
24720
23525

Heat Rate (BTU/HP.Hr)
6906**
6985
7078
7181
7298

PT Speed (RPM)
4800
4800
4800
4800
4800

PT Exit Flow (lb/s)
152.4
147.9
143.5
139
134.4

NOx (vppm)
25
25
25
25
25

NOx (tons/yr)
95
92
90
87
84

CO (vppm)
5
5
5
5
5

CO (tons/yr)
12
11
11
11
10

Guarantee Tolerances:

*Output Power (HP)

0%

**Fuel Rate (BTU/HP-Hr)

+3%

Guarantees are based on a clean and new engine.  All other data is expected, not guaranteed. 

Note:    

1)
Tons/yr based upon 8760 hours per year and 1 ton = 2000 lb.

Enron-Transwestern, MC0098-01
February 14, 2001


