OFFSHORE POWER OPERATIONS C.V.

DABHOL POWER PLANT,

GUHAGAR, RATNAGIRI.


INCIDENT REPORT – Naphtha Spill. 

1. Facility name: Fuel Filter Skid

2. Location:  Day Tank Area

3. Date of Incident: 19/03/2001

4. Time of Spill Occurrence or Discovery: 00:45 am                  

5. Name of Reporter: Security Guard

6. Material Released to: Oil/water separator and to storm water Drain. 

7. Description of Incident: There was mal-functioning of one of the solenoid valve in the water drain line (3/4”) in fuel filter skid D & E. This lead to the draining of naphtha through the line leading to Oil/Water Separator and finally some naphtha along with water could find its way to storm water drain leading to one of the silting basin within plant property line.

8. Injuries or Property Damage: None

9. Clean-up/Containment Actions: Oily water passing through the storm water drain was contained before reaching to silting basin by putting temporary bund. There after oily water were absorbed in absorbing pads and pillows. 

Shift Manager:____________ Signature:____________ Date:___________

