[image: image1.wmf]  ISO 9001 CERTIFIED
TECHNICAL PROPOSAL INFORMATION

Customer:
S & S Energy Products

Date:
10/02/00

Proposal No:
-

Spec No:
-

Item No:
Q793001/A

RATING

Type
Transformer
Class
H Winding
X Winding
Y Winding

Phase
3
-
60 Wye
kV
13.8 Delta
kV
-
kV

Hertz
60
OA
36,000
KVA
36,000
KVA
-
KVA

Temp Rise
65 °C
FA
48,000
KVA
48,000
KVA
-
KVA

Insul Liquid
NON PCB OIL TYPE I
FA
60,000
KVA
60,000
KVA
-
KVA


-
-
-
KVA
-
KVA
-
KVA

ADDITIONAL TAP VOLTAGES

H Winding  (Kv)
± 2 of 2.5 %
NLTC

X Winding  (Kv)
-
 

 
 


CONNECTIONS FOR OPERATION

Transformers in Bank
To Transformer From
Phase
Connected
To Transformer To
Phase
Connected

-
-
-
-
-
-
-


PERFORMANCE BASED

ON A LOADING OF

H Winding
60.0
kV
36.0
MVA

X Winding
13.8
kV
36.0
MVA

Y Winding
-
kV
-
MVA

-
-
-
-
-

-
-
-
-
-


DIELECTRIC TESTS



Applied Voltage
H Winding
34
kV

(To other wind-
X Winding
34
kV

ing and ground)
Y Winding
-
kV

Induced
7200 cycles
120
kV

Voltage
 
-
kV

INSULATION LEVELS


Basic Lightning
Low Frequency

ITEMS
Impulse Insula-
Voltage


tion Level
Insulation Level

H Line
350
140

H neutral
110
34

X line
110
34

X neutral
-
-

Y line
-
-

PERFORMANCE DATA, Based on
85
(C Reference Temperature,
36
MVA     Altitude:  1000  Mts.

Losses and Exciting Current
Regulation

Excitation
% Ex
No Load Kw (20°C)
Total Loss   Kw
Power Factor
% Regulation

100%
0.5
28
155
0.80
5.280

110%
2.208
39 *
166 *
1.0
0.671

-
-
  * Not Guaranteed

-
-

AUXILIARY LOSSES

Transformer KVA
Class
KWatts Aux Loss

36,000
-
OA
0

48,000
-
FA
4

60,000
-
FA
5.5

-
-
-
-

-
-
-
-

Average Sound Level
74/76/77
dB   OA/FA/FA

PERCENT IMPEDANCE VOLTS


Between
At
% IZ
Between
At

% IZ
Windings
kVA
Zero
Windings
kVA

8
H-X
36,000
6.8
H-X
36,000

-
-
-
-
-
-

-
-
-
-
-
-

EFFICIENCIES   ( p.f = 1 ) AT 36 MVA





Load
Full Load
3/4 Load
1/2 Load 
1/4 Load

%
99.576
99.638
99.675
99.612

MECHANICAL DATA

Not for Construction Purposes

Outline Dwg No:
Q793A100




Dimensions (Approximate)                            Ft.  (Mts.)

Height
(A)
17.8 (5.42)


Width
(B)
22.3 (6.80)


Depth
(C)
14.9 (4.55)


Height over Cover
(D)
13.0 (3.95)


Untanking (Plus slings)
(E)
23.3 (7.10)


Shipping Dimensions:Ft
W x D x H
12.7 x 9.6 x 13


Masses (Approximate)                              pounds   (Kg)

Core and Coils

59,190 (26,850)


Tank and Fittings

32,410 (14,700)


Liquid
  4,910
GL 
36,930 (16,750)


Total Mass

128,530 (58,300)


Shipping without OIL

79,480 (36,050)


Shipping with OIL

109,240 (49,550)


