Status No.
Description
Theoretical Error Identification
Actual Error Identification
Theoretical Availability Counter
Actual Availability Counter

1
program start PLC
PLC was freshly started
Same
Turbine OK
Turbine OK

2
no error
turbine free of error
Same
Turbine OK
Turbine OK

3
manual stop
manual stop from switching box key or turbine PC (general control function or DI1.13=0 (Bvb =1)  or DI11.11=0 (BvB=1) )
Same
Turbine OK
Turbine OK

4
remote stop
manual stop from remote PC (general control function)




5
remote start
turbine start from remote PC (general control function)




6
system OK
no error and no manual stop
Same
Turbine OK
Turbine OK

7
storm shutdown
wind P6.5 time averaged P6.6 exceeded or
Same—wind P6.6 exceeded for P6.5 time average
Weather Downtime
Weather Downtime



wind P6.7 exceeded for period P6.8 or
Same
Weather Downtime
Weather Downtime



blade angle below P12.10 for a period P6.8
P12.10 is “max time(ms) for blade asymmetry.”

P12..8 is “max time(ms)  for blade angle deviation.”
Weather Downtime
?

8
Overvoltage
one of the line voltages exceeded P20.1for a period P20.7 
Same
Line Out Time
Grid Downtime

9
Undervoltage
one of the line voltages below P20.1for a period P20.7
Error cannot be generated with this condition



13
Asymmetric generator current
2 current phased deviate from one another by P20.5 for more than 500 ms
Same
Downtime
Downtime

14
generator overspeed
generator speed below P1.1 for a period of  P1.2 
 Same—set P1.1 < 1600rpm
Downtime
Downtime

15
rotor overspeed
rotor speed below P1.3 for a period of  P1.4 
Same—set P1.3 < 23rpm
Downtime
Downtime

16
Rotor speed monitor
overspeed on (rotor) monitor, Ind. proximity switch between gearbox and generator (DI12.11 =1)
Same—also triggered status msg. No. 63 when DI12.11 = 1
Downtime
Downtime

17
Centrifugal switch 
overspeed on centrifugal switch (DI11.18=1)
Same—also triggered status msg. No. 63 when DI12.18 = 1
Downtime
Downtime

19
maximum motor power
power below P4.10 for 1 sec 
Same
Downtime
Downtime

20
cable twisting right
P11.5 rotations spinning or P11.6 rotations in all states exceeded
Same
Turbine OK
Turbine OK

21
cable twisting left
P11.5 rotations spinning or P11.6 rotations in all states exceeded
Same
Turbine OK
Turbine OK

22
yaw drive end position
nacelle rotations P11.7 exceeded
Same
Downtime
Downtime

23
Peak value for excessive output 
power  P4.2 exceeded for period P4.3 
Same
Downtime
Downtime

24
primary braking time too long
blade drive time P8.7 for type 2 braking to feathered pitch position or speed not under 80 rpm in time P8.7




25
no speed reduction with primary braking (pitch)
no reduction in generator speed with braking types 3-5 after the first 5 sec, after 0.5 sec thereafter and not below 300 rpm

Downtime
Downtime 

27
secondary braking time too long
not below speed of 80 rpm after a period P8.6 after application of brake 




28
no speed reduction with secondary braking 
no reduction in generator speed with braking types 6-7 after the first 5 sec, after 0.5 sec thereafter and not below 300 rpm




31
timeout yaw counter 
for azimuth adjustment there is no pos. gear drive – signal flank (DI11.1) within a period P11.9 




34
brake not released

secondary brake
after period P9.6 following opening of the brake, the brake is not released (DI12.3=0) for a period of  P9.9




35
Emergency stop
emergency off button activated in control box (DI1.4=1)
Same—also triggered status msg. No. 63 
Downtime
Downtime

36
speed with braked turbine
below gen. speed 14 rpm / rotor speed 1.5 rpm 30 sec after application of brake




38
secondary brake test
brake test after 1400 h below power 500 kW without pitch brake




41
vibration sensor defect
monitoring accelerometer (PCH):

error signal DI11.32 = 0 or accel. with braking < test level (P7.11) or test brake < 2,5 m/s² 
DI11.32 = 0 no error was generated
Downtime
?

42
wrong yaw drive direction
identification of wrong direction : apply brakes immed. and reset timer / counter. 1.: no fault message, 

2.: shut down turbine with EM 42, 

3.: stationary at v = v3 block restart, block azimuth for v > v3 - 5 m/s,

4.: stationary at v < v3 - 5 m/s EM 42 must be manually acknowledged, azimuth is blocked.

If the rotational direction is correct for the trials 1-4, start the turbine and disturbance message 42 is withdrawn. 
?
Downtime


43
Hydraulic filter polluted (switch off)


Downtime


44
Hydraulic filter polluted (warning)


Turbine OK


45
hydraulic pump time too long
hydraulic pump period above P9.5 (no EDS-built up in the period)
DI12.4 = 0
Downtime
Downtime

46
hydraulic pump (interval) time too short
hydraulic pump interval period below P9.4 




47
hydraulic service switch top cabinet
Hydraulic service switch  activated (DI11.14=0)
Same
Maintenance period
Maintenance period

48






51
gearbox oil level too low
Gearbox oil level too low and gearbox temp. exceeded by 5°C for period P10.2 (DI12.5=0)
DI12.5=0 no fault generated
Downtime
?

52
gearbox oil pressure too low
Gearbox oil pressure too low for a period P10.1 delayed for a period P10.8 after switching on pump (DI12.9 = 0)
Same
Downtime 
Downtime 

53
wind vane defect
Azimuth adjustment angle 200° exceeded and no flank change in center signal (DI11.8)

Downtime


54
anemometer defect
Power P6.9 exceeded for period P6.10 and wind less than 4 m/s for period P6.10 

Downtime


55
rotor pulse sensor defect
no rotor pulse (CNT11.8) for 10 sec, if rotor speed below P1.11 

Downtime


56
gen. pulse sensor defect
no rotor pulse (CNT11.11) for 10 sec, if rotor speed below P1.11/P1.5 

Downtime


57
ratio generator/rotor speed
Deviation P1.6 generator /rotor speed for period P1.7 exceeded

or immediate generator speed signal value failure
Same
Downtime
Downtime

58
Demand to stop by an external. device
DI1.27=0 
Same 
External stop period
External stop period

59
vibration switch
vibration switch activated (DI11.9=1)
Same—also triggered status msg. No. 63
Downtime
Downtime

60
yaw limit switch activated 
azimuth limit switch activated (DI1.15=1)
Same
Downtime
Downtime

61






62
PLC fault collection
failure fast bus communication to PLC slave at top box

Downtime


63
safety chain
safety chain activated (DI1.14=0)
Same—also can be triggered along with msg. No. 16, 17, 35, 59
Downtime
Downtime

64
motor protection
motor protection control box MFR13 activated (DI1.5=0)
Same 
Downtime
Downtime

65
main switch activated
power switch activated (DI1.2=1)
Same
Downtime
Downtime

71
gearbox oil soiled 

(shutdown)
filter soiled (course) for period P10.6 (DI12.7=1) 
Same
Downtime
Downtime

72






75
generator bearing A 

overtemperature
temperature above P13.4 for 60 sec, restart: 

temperature under P13.4 - 15°C 
Same
Downtime
Downtime

76
generator bearing B 

overtemperature
temperature above P13.5 for 60 sec, restart: 

temperature under P13.5- 15°C
Same
Downtime
Downtime

77
gearbox oil 

overtemperature
temperature above P13.8 for 60 sec, restart: 

temperature under P13.8 - 15°C
Same
Downtime
Downtime

78
outside temperature too low
temperature above P13.10 for 60 sec, restart: 

temperature under P13.10 - 15°C
Temperature below P13.10 for 60 sec, 
Weather Downtime
Weather Downtime 

81
shaft bearing overtemperature
temperature above P13.12 for 60 sec, restart: 

temperature under P13.12 - 15°C (only from EW1.5s)
Same
Downtime
Downtime

82
yaw motor

overtemperature
one of the 3 PTC-temperature sensors on the azimuth motors report excessive temperature (> 155°C) (DI11.3=0) 
Same
Downtime
Downtime

83
gearbox bearing B overtemp. (only offshore)
temperature above P13.13 for 60 sec, restart: 

temperature under P13.13 - 15°C
No fault was generated when temperature above P13.13
Downtime
?

84
gearbox oil temp. to low
temperature below P13.7 for 60 sec, restart: 

temperature above P13.7 + 5°C 
No fault was produced
Downtime
?

86
Brake pads worn,  secondary brake
brake lining worn for 20 sec (DI12.2=0)
Same
Downtime
Downtime

87
restart time delay
set after grid loss, temperature errors, storm and calm, period P8.1
Same
Turbine OK
Turbine OK

88
multiple overtemp. Shutdown
display. P13.11 temp. errors 75-77, 81, 98-100, 103, 107, 115,139 exceeded
Same
Downtime
Downtime

89
gearbox oil dirty (warning)
filter soiled (fine) for period P10.6 (DI12.6=1)
DI12.6=1 no fault generated
Turbine OK
?

94
control call
parameter P23.6 > 0 causes an error number to be set for 30 sec.
Same
Turbine OK
Turbine OK

95
PC restart
180 sec after fresh PC reset set the message for 60 sec via Watchdog function 




97
generator cooling air

overtemperature
temperature above P13.6 for 60 sec, restart: 

temperature below P13.6 - 15°C
Same
Downtime
Downtime

98
gearbox bearing overtemperature
temperature above P13.9 for 60 sec, restart: 

temperature below P13.9 - 15°C
Same
Downtime
Downtime

99
generator 1 overtemperature
temperature above P13.1 for 60 sec, restart: 

temperature below P13.1 - 15°C
Same
Downtime
Downtime

100
generator 2 overtemperature
temperature above P13.2 for 60 sec, restart: 

temperature below P13.2 - 15°C
Same
Downtime
Downtime

101
motor protection fuse
24V fuse protection in control box activated (DI1.6=0)
Same
Downtime
Downtime

102
motor protection top cabinet
motor protection top cabinet activated (DI1.7=0)
Same
Downtime
Downtime

103
generator 3 overtemperature
PTC-temperature generator sensor reports overtemp. (DI12.14=0)

(for BvB and first Bachmann  turbines not yet wired!)
Same
Downtime
Downtime

104






105
Rotor CCU fault voltage
voltage error, pulses (generator side)  (DI1.19=0)
Same
Downtime
Downtime

106
Rotor CCU fault current
current error, pulses (generator side)  (DI1.20=0)
Same
Downtime
Downtime

107
Rotor CCU fault temperature
temperature error, pulses (generator side) (DI1.21=0)
Same
Downtime
Downtime

108
rotor locking
one of the rotor locks is engaged (DI12.10=1)
Same—also triggered msg. No. 63
Maintenance period
Maintenance period

109
gen. carbon dust filter dirty
filter soiling for period P8.4 (DI11.20=1)
Same
Turbine OK
Turbine OK

110
speed in tower resonance range
generator speed in tower resonance range P1.8 - P1.9 for period P1.10

Turbine OK
Turbine OK

112
Response signal from CCU
control (DO1.13) and (acknowledgement freq. converter (DI1.18) AND acknowledgement Main switch (DI1.3)) differ for 65 sec




113
Line CCU fault voltage
voltage error pulses (line side)  (DI1.22=0)
Same
Downtime
Downtime

114
Line CCU fault current
Current error pulses (line side)  (DI1.23=0)
Same
Downtime
Downtime

115
Line CCU fault temperature
Temperature error pulses (line side)  (DI1.24=0)
Same
Downtime
Downtime

116
line fault voltage


Line voltage error (DI1.25=0)
Same
Line out time
Grid Downtime 

117
Line fault frequency 
Line frequency error (DI1.26=0)
Same
Line out time
Grid Downtime

118
EMERGENCY STOP

TOP-BOX
Emergency off top-box/hub activated (DI11.16=1)
Same—also triggered msg. No. 63
Downtime
Downtime

119
pitch controller timeout
10 timeout periods of 150 ms exceeded from pitch controller




120
communication fault pitch controller
6 communication errors in receipt package from pitch controller




121
axle disturbance 1 

pitch controller
pitch controller reports axle disturbance for a period P12.12 (axle state bit 7=1)




122
Collective fault pitch controller
pitch controller reports unit disturbance for a period P12.12 (axle state bit 7=1)




123
gearbox oil cooler switch contact
gearbox oil (60 °C) exceeded for 1 sec (DI12.40=1), not for EW1.5s




124
Pitch overrun 0°
at least. 1 rotor blade at limit switch (-10°) (DI11.28=0)
DI11.28=1
Downtime
Downtime

125
Pitch overrun 90°
at least. 1 rotor blade at limit switch (90°) (DI11.27=0)
DI11.27=1
Downtime
Downtime

129
generator speed implausible
deviation P1.6 generator / gearbox speeds exceeded for. period P1.7 
Same
Downtime
Downtime

130
braking time blade 1 too high
drive time P8.5 exceeded for blade 1 for battery shutdown to the feathered pitch position




131
braking time blade 2 too high
drive time P8.5 exceeded for blade 2 for battery shutdown to the feathered pitch position




132
braking time blade 3 too high
drive time P8.5 exceeded for blade 3 for battery shutdown to the feathered pitch position




133
battery charging 

rotor blade drive
Battery charging at standstill for period 8.8 after message ‘battery voltage too low’ or ‘braking time blade 1, 2 or 3 too long’ after battery test double the time 




134
battery charging voltage not o.k.
Battery charging voltage not o.k. (DI11.29 = 0) or (until V1xx25) batt. Voltage too low (input 5 for each controller axis = 0, see P25.1-3)
Same
Downtime
Downtime

135
battery test
Battery test every 700 h, when the wind below 3.5 m/s




136
Limit switch rotor blade 0° defect
Message blade at limit switch (DI11.28=0) and blade angle > 0°




137
limit switch rotor blade 90° defect
Message blade at limit switch (DI11.27=0) and blade angle (  feathered pitch position




138
Temperature warning

pitch motor
Warning temp exceeded for at least 1 pitch (bit 1 dig input pitch controller=0)




139
Overtemprature

pitch motor
max. temp exceeded for at least 1 pitch (bit 2 dig input pitch controller=0)




140
motor protection

pitch motor
motor protection activated from at least one pitch motor (bit 1 dig input pitch controller=0)




141
Rotor CCU collective fault 
other errors PWR (DI1.19=0, DI1.20=0, DI1.21=0)
Same
Downtime
Downtime

142
line CCU collective fault 
other errors NPR (DI1.22=0, DI1.23=0, DI1.24=0)
Same
Downtime
Downtime

143
Pulse sensor rotor monitor defect
no pulses (DI12.1) to overspeed monitor for 10 sec, if gen. speed P1.11 is exceeded




144
blade angle asymmetry
deviation P12.9 of 2 blade angles for a period P12.10 or 4° for 200ms exceeded in pitch automatic mode
Same
Downtime
Downtime

145
blade pitch control deviation
deviation P12.7 of blade angle current value and demand for a period P12.8 or in excess of 10° for 200 ms in controlled pitch operation.. When braking 6 times the deviation from P12.7 is allowable
Same
Downtime
Downtime

146
turbine stopped due to calm
below 15% of speed P2.1 when spinning, 30 sec time delay, reset for exceeding wind 3.5 m/s at standstill

Weather Downtime
Weather Downtime

147
load shutdown
command load shutdown from turbine PC or remote PC causes shutdown in feathered pitch position
Same
Turbine OK
Turbine OK

148
generator fan service switch
service switch gen. fan activated on top-box (DI11.15=0)
Same
Maintenance period
Maintenance period

149
Axle 2 fault, pitch controller
pitch controller reports axle disturbance 2 for period P12.12 (axle state bit 7=1)




150
Axle 3 fault, pitch controller
pitch controller reports axle disturbance 3 for period P12.12 (axle state bit 7=1)




151
Responce circuit breaker generator brush
Not used in USA/Spain




152
Obstruction light

Error/failure
if twilight switch (DI11.22) = 1 and no appearance of a 24V signal of 24V-supply or fault/failure signal of Reetec device within 30 sec (DI11.23 / DI11.24 = 0)

monitoring twilight switch : If  P26.3 Bit6 = 1 and between. 11 PM and 3 AM  DI11.22 = 0 for 30 sec, then FM152, too. (from V1xx26)
Fault Message 216 is also triggered when DI11.22=1
Turbine OK
Turbine OK

153
brush wear generator
brush limit switch reports excessive wear (DI11.19 =0)  (from turb. 3), after a period P8.11 the turbine is braked
Same
Turbine OK
Turbine OK

154
generator cooling water pressure/level not ok
only for EW1.5/70.5 (Tehechapi)  monitor generator water cooling  (DI11.21=0), if P26.3 Bit 0 = 1
No fault generated with P26.3 Bit 0=1 and DI11.21=0
Downtime
?

155
maintenance
service rotary switch is set to the ‘maintenance’ position (DI1.29 = 1). No remote commands will be carried out. With a start command the turbine will restart for 30 minutes.
Same
Maintenance period
Maintenance period

156
repair
service rotary switch is set to the ‘repair position (DI1.30 = 1).. No remote commands will be carried out. With a start command the turbine will restart for 30 minutes.
Same
Repair period
Repair period

157
brake does not close
1 sec after applying the brake message that brake still released (DI12.3=1) 




161
Overvoltage protection triggered
The overvoltage protection device in main (DI1.16=0) or 

top switch cabinet (DI11.30=0) is faulty and can not make sure any overvoltage protection
Same
Downtime
Turbine OK

162
fault battery charge switching
charge switching relays stay 2h = 1 (dig. Input 7 axis 2 at controller)




163
torque

deviation
assigned torque demand and power are implausible.

Deviation converted to kW : 200 delayed by 30 sec




164
maintenance switch pitch
a maintenance switch on the axle box separates the batteries from pitch motor (DI11.26= 0)




165
service switch pitch
switch setting at the control box Hub is in manual operation, blade adjustment is possible from the controller, without an error or assigned demand from the PLC (dig. Input 7 axis 1 at controller)




166
Normal operation
Signals end of :  low noise operation, stop by an external device, ice alarm, Direction dependent shut-down
Same 
?
Turbine OK

167
voltage limitation activated
voltage is limited by assignment of an inductive reactive power < 1, phi < 0° and /or power limitation  




168 
Reserve





169
waiting for gearbox oil pressure
when oil pump on (DO11.10=1), P10.1 (delay time oil pressure gearbox) > 70 sec and curr. delay time > 5 sec.

Note: why the turbine does not yet start after the START button has been activated




170
increasing speed with falling blade angle
Monitoring pitch / generator speed gradient :

50ms-averaged speed increases with falling blade angle -> delays for period P26.5 in ms, FM170 remains set for 2 sec 




171
service key brake release
when activating the button ‘release brake’ at the top-box  (DI11.13=1) in the feathered pitch position. Message remains 30 sec after releasing the button
Same
Turbine OK
Maintenance period 

172
Ice sensor alarm 
The ice sensor detects or indicates low temperature and high humidity. Maybe there is ice at the rotor blades.
DI12.16=1
External stop period
External stop period

173
low-noise operation
turbine runs at lower speed and power, cleared through P27.1. ‘max. rotor speed low-noise’ operation and activated via input DI1.31=1




174
overtemp. Transformer warning 
input DI2.7 = 1 for 30 sec, signal from PTC resistor activation device MSF220K (offshore) or transformer temperature > P13.17, if Bit5=1 of P23.6, automatic reset below P13.17-15°C




175
overtemp. transformer

disturbance
input DI2.8 = 1 for 30sec, signal from PTC resistor activation device MSF220K (offshore) or transformer temperature > P13.18, if Bit5=1 of P23.6, automatic reset below P13.18-15°C




176
drive train vibration
drive train acceleration > f(P7.9, v_wind) for period P7.10 and P7.12 bit 2 = 1 or Bit 15 = 1, from V1x023 :

f = fmin = 100 * trunc(P7.9/100)  for v_wind < vmin =trunc(P7.4),

f = fmax = fmin + 100*(P1.9-fmin) for v_wind > vmax = trunc(P7.4) + 10* (P7.4 - trunc(P7.4)),

f = fmin + (v – vmin ) * ( fmax – fmin) / (vmax – vmin) else

Downtime
Downtime

177
tower vibration
Accelerometer monitors the frequency range around the tower’s resonance frequency (approx. 0.28 Hz) and alarms (DI11.31=0 and P7.12 bit 1 =1) or tower acceleration > P7.7 for period P7.8 and P7.12 bit 0 = 1 (for large / soft towers >= 80m) 
Same
Downtime
Downtime

180
wind deviation
1sec-average wind direction deviation value > P7.5 (60°) or

10sec average value > P7.6 (40°) and

4min- average wind speed > 7 m/s




181
Idling position
turbine in spinning mode

Turbine OK
Turbine OK

182
start up
turbine starting up / no/load mode

Turbine OK
Turbine OK

183
load operation
turbine in load operation

Turbine OK
Turbine OK and Operation period 

184
shutdown
turbine shutdown (braking)

Turbine OK
Turbine OK

185
manual operation pitch
Manual blade adjustment with pitch rate P12.5 (control function –blade angle or operating function at the top-box operating device )
Same
Turbine OK
Maintenance period

186
manual operation speed
Manually assigned generator speed in idling mode (control function -speed)
Same
Turbine OK
Maintenance period

187
manual operation torque
Manually assigned torque in load operation (control function –freq. Converter), if 30min manual operation  the turbine is braked
Same
Turbine OK
Maintenance period

188
Manual operation, line seperation
manual grid separation (control function – frequency converter)

speed control to setpoint P3.4 in idling mode, if 30min manual operation  the turbine is braked
Same
Turbine OK
Maintenance period

189
manual operation yaw
manual azimuth adjustment or azimuth blocking with service switch (control function – general, operation function at operating panel at top-box) DI1.10 = 1, DI1.11 =1 or DI11.10 =1), if 30min manual operation  the turbine is braked
Same
Turbine OK
Maintenance period

190
temperature error container


Temperature below P13.14 for 60 sec or temperature above P13.15 for 60 sec, reset temperature over P13.14 + 5°C and below P13.15 – 5°C (offshore only)




191 
manual operation gen. fan
in manual operation from PC (local or remote) or operating device, fan is then permanently on or off, if 30min manual operation  the turbine is braked

Turbine OK
Maintenance period

192
Wrong parameter check sum
At PLC restart the remanently stored parameters are checked according consistency of check sum. If there is any differences the default values are loaded. This message 192 shall remark to it, the tuirbine is blocked for run-up. Message remains set, until the release parameter (P26.12) and the tower resonce parameter (P1.8/9) are set correctly and the message is reset by the operator.




193
marine obstuction light
if twilight switch (DI11.22) = 1 DI12.15 (prewarning) or DI12.16 (failure) =0 longer than 30sec (offshore only)




194
by-pass filter soiling 
if oil sump temp. > (P14.13 + P14.14)/2 (by-pass filter pump DO11.14 =1) and DI12.8 = 1 longer than 5 mins. -> shutdown by-pass filter pump DO11.14 =0




195
gearbox pressure loss by-pass filter 
if by-pass filter pump P11.14=1 and DO11.14 =1 and DI12.12 = 0 (pressure switch) longer than 10 sec -> shutdown by-pass filter pump DO11.14 =0




196
Pre-heating fault CCU cooling system 
No increasing of CCU cooling system temp. by 3K during 150s of pre-heating (offshore only)




197
Overtemp.  CCU cooling system 
Temperature above P13.15 for 60 sec, restart: 

Temperature below P13.15 - 15°C  (offshore only)




198
pressure fault CCU cooling system 
IF pump1= on OR (pump2 = on AND valve 1,2 = on) AND DI2.1 = 0 (pressure switch) THEN FM198 (5sec delayed) 
(offshore only)




199
test fault CCU cooling system 
Not enough pressure (DI2.1=0) during self test at turbine start 

(offshore only)




200
Pre-heating CCU cooling system active
Preheating CCU cooling system active (offshore only)




201
PLC fault 24V supply
The external 24V-power supply is failed at least one module of the control unit. (except DO216, DO232); possible error also defect module at 24V-side

More details via  P24.8, P24.9




202
PLC module failure
There is a fault at at least 1 module of the control unit. (except power supply, CPU module)

More details via  P24.8, P24.9




203
Fault temperature measurement
All temperature measurement at the PTAI module are constant for 10 minutes (resolution 0.1°).




204
FastBus Service Mode
From SW vers. 1x023 the PLC is configured without any reboot when there occures a fast bus communication error. The communication to the slave is retried again only after a manual reboot of the PLC master. For service purposes the setting can changed by the M-Manager to:

· Reboot at Slave failure

· Reboot at slave detection

With these settings FM204 appears.




205
overtemperatur TopBox

(EW900 only)
temperature above P13.15 for 60 sec, restart: 

temperature below P13.15 - 15°C 




206
Gearbox pressure too high

(EW900 only)
DI12.12 = 1




207
Ground fault LVMD

(EW1.5/70.5(60Hz) only)
DI1.32 = 1 , FM207 delayed by P20.13 






208
No Activity CAN-Bus CCU
Live pulse (Togglebit 15 in status word P29.1) stays constant for a period of 150ms  -> CAN-Bus connection broken / disturbed or CCU switched off.




209
No activity CAN-Bus MFR13
Multiplex number for CAN bus data from MFR13 (grid monitor device) stays constant for a period of 300ms  -> CAN-Bus connection broken / disturbed or MFR13 switched off.




212
Battery voltage low axis 1
Battery voltage too low axis 1 (input 5 f. axis 1 at pitch controller = 0, s. P25.1 und P25.9), from V1xx26




213
Battery voltage low axis 2
Battery voltage too low axis 2 (input 5 f. axis 2 at pitch controller = 0, s. P25.1 und P25.9), from V1xx26




214
Battery voltage low axis 3
Battery voltage too low axis 1 (input 5 f. axis 3 at pitch controller = 0, s. P25.1 und P25.9), from V1xx26




215 
Direction dependent shut-down
Nacelle position is inside the direction range defined by P27.4-8 and P > P27.9 or v > P27.10, restart if v < P27.11 or Nacelle position is outside the direction range. from V1xx26




216
obstruction light switch over to auxiliary lamps
If DI11.25 = 0 for 30 sec with activated twilight switch (DI11.22 =1), then FM216, main lamps are defect, but obstruction light is still on with auxiliary lamps 
Same
Turbine OK
Turbine OK

217
End of parameter state service
After switching over of service switch to automatic the turbine stops after temporary parameter modification with service dongle or access.

After restart of the turbine the old parametrs are loaded again .




218
Frequent cut-ins
For a period of one hour and one day the nunber of activations of synchr.switch are counted. If these quantities are grater than P26.13 or P26.14, the turbine is switched-off with message 218. Suspicion on wrong parameter settings (no hysteresis switching-on/off !)




219
Ice sensor fault
DI 12.15 = 0 for 2 min and P26.3 Bit 8 = 1, ice sensor indicates an error : sensor- or LID-Controller fault




220
External Stop caused by curtailment
External command from park-PC with monitoring of curtailment,

because of turbulences some of turbines standing too close to each other should be switched off . 




221
External power limitation 
External command from park-PC with max. power demand




