PAGE  

[image: image1.wmf]
URGENT Technical Advisory

2000-005
Subject: Emergency Seal Oil DC Motor
 Date: June 13, 2000

PROPRIETARY INFORMATION

This document contains information proprietary to Siemens Westinghouse Power Corporation, A Siemens Company.  Your acceptance of it is an acknowledgment of a confidential relationship between you and Siemens Westinghouse Power Corporation.  It is to be used solely by you for the purpose for which it is furnished and is to be returned or destroyed when no longer required for that purpose.  Neither this document nor any information obtained therefrom is to be reproduced, transmitted, disclosed, or used otherwise in whole or in part without the written authorization of Siemens Westinghouse Power Corporation.

  Approved:  [image: image2.png]LLATT S rceer




R.T. Werner

Siemens Westinghouse Power Corporation

DISCLAIMER OF WARRANTIES
AND LIMITATION OF LIABILITY

THERE ARE NO UNDERSTANDINGS, AGREEMENTS, REPRESENTATIONS, OR WARRANTIES, EXPRESSED OR IMPLIED, INCLUDING WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE, OTHER THAN THOSE SPECIFICALLY SET OUT IN ANY EXISTING CONTRACT BETWEEN THE PARTIES REGARDING THIS EQUIPMENT. ANY SUCH CONTRACT STATES THE ENTIRE OBLIGATION OF SELLER. THE CONTENTS OF THIS DOCUMENT SHALL NOT BECOME PART OF, OR MODIFY ANY PRIOR, OR EXISTING AGREEMENT, COMMITMENT, OR RELATIONSHIP.

The information, recommendations and descriptions in this document are based on Siemens Westinghouse's experience and judgment with respect to this equipment's operation and maintenance. THIS INFORMATION SHOULD NOT BE CONSIDERED AS ALL INCLUSIVE OR COVERING ALL CONTINGENCIES. If further information is required, Siemens Westinghouse Power Corporation should be consulted.

NO WARRANTIES, EXPRESSED OR IMPLIED, INCLUDING WARRANTIES OF FITNESS FOR A PARTICULAR PURPOSE OR MERCHANTABILITY, OR WARRANTIES ARISING FROM THE COURSE OF DEALING, OR USAGE OF TRADE, ARE MADE REGARDING THE INFORMATION, RECOMMENDATIONS, OR DESCRIPTIONS CONTAINED HEREIN.  In no event will Siemens Westinghouse be responsible to the user in contract, in tort (including negligence), strict liability or otherwise for any special, indirect, incidental, or consequential damage or loss whatsoever, including, but not limited to damage to, or loss of use of equipment, plant, or Power system; cost or capital; loss of profits or revenues; cost of replacement Power; additional expenses in the use of existing Power facilities; or claims against the user by its customers, resulting from use of the information, recommendations, or descriptions contained herein.

1. REASON FOR advisory
NOTICE AND WARNING:

THE RECOMMENDATIONS AND ADVICE GIVEN IN THIS TA ARE INTENDED TO ADDRESS A POTENTIAL GENERATOR HYDROGEN GAS EXPLOSION HAZARD.  FAILURE TO FOLLOW THESE RECOMMENDATIONS MAY RESULT IN SERIOUS LOSS, OR DAMAGE TO THESE PRODUCTS OR OTHER PROPERTY, OR PERSONAL INJURY, OR DEATH.

It has been determined that in the event of AC Power failure, the emergency seal oil DC motor of Siemens Westinghouse/Westinghouse 501D and 501F models: 

1. with modular inner cooled generator;

2. with conventional cooled generator;

3. with 30 psi single flow seal oil systems generator

may not perform to rated speed (1750 rpm) and output (12.2 gpm, 55-75 psig) for extended periods.

2. Technical Recommendation
WARNING:

IF AC POWER LOSS ON THESE UNITS OCCURS, THERE IS A POTENTIAL FOR HYDROGEN GAS EXPLOSION.

Corrective action is to replace the emergency seal oil DC motors with a 125 V DC armature and field.  SWPC has organized an orderly retrofit program and will notify operators of the availability of replacement motors.  Operators are urged to carefully monitor the status of their current DC motors until availability of the replacement during the next scheduled outage, routine maintenance interval, or forced shutdown.

Until the corrective action has been accomplished, in addition to all other safety procedures and precautions, affected sites must:

1. Prohibit:

a. entry into the turbine enclosure;

b. access to generator platform;

c. access to generator piperack;

d. access to all areas at collector end of generator within 20 ft.

2. Record and submit to SWPC representative all nameplate information from the emergency seal oil DC motor to confirm actual motor rating.

Contact SWPC representative:

Mark Johnson

Phone (407) 736-2651







Fax 
 (407) 736-5007

3. Change WDPF or TXP Combustion Turbine Control Logic to include automatic H2 venting (vent down at least to 10 - 15 psig) in case of AC Power loss.
















OP0103

TA2000-005

© 1999 Siemens Westinghouse Power Corporation

             A Siemens Company

