[image: image1.wmf]
Technical Advisory

2000-014
Subject: Replacement of W501F Row 3 

Turbine Blades
Date: October 17, 2000

PROPRIETARY INFORMATION

This document contains information proprietary to Siemens Westinghouse Power Corporation, A Siemens Company.  Your acceptance of it is an acknowledgment of a confidential relationship between you and Siemens Westinghouse Power Corporation.  It is to be used solely by you for the purpose for which it is furnished and is to be returned or destroyed when no longer required for that purpose.  Neither this document nor any information obtained therefrom is to be reproduced, transmitted, disclosed, or used otherwise in whole or in part without the written authorization of Siemens Westinghouse Power Corporation.

  Approved:  [image: image2.png]LLATT S rceer




R.T. Werner

Siemens Westinghouse Power Corporation

DISCLAIMER OF WARRANTIES
AND LIMITATION OF LIABILITY

THERE ARE NO UNDERSTANDINGS, AGREEMENTS, REPRESENTATIONS, OR WARRANTIES, EXPRESSED OR IMPLIED, INCLUDING WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE, OTHER THAN THOSE SPECIFICALLY SET OUT IN ANY EXISTING CONTRACT BETWEEN THE PARTIES REGARDING THIS EQUIPMENT. ANY SUCH CONTRACT STATES THE ENTIRE OBLIGATION OF SELLER. THE CONTENTS OF THIS DOCUMENT SHALL NOT BECOME PART OF OR MODIFY ANY PRIOR OR EXISTING AGREEMENT, COMMITMENT, OR RELATIONSHIP.

The information, recommendations and descriptions in this document are based on Siemens Westinghouse's experience and judgment with respect to this equipment's operation and maintenance. THIS INFORMATION SHOULD NOT BE CONSIDERED AS ALL INCLUSIVE OR COVERING ALL CONTINGENCIES. If further information is required, Siemens Westinghouse Power Corporation should be consulted.

NO WARRANTIES, EXPRESSED OR IMPLIED, INCLUDING WARRANTIES OF FITNESS FOR A PARTICULAR PURPOSE OR MERCHANTABILITY, OR WARRANTIES ARISING FROM THE COURSE OF DEALING OR USAGE OF TRADE, ARE MADE REGARDING THE INFORMATION, RECOMMENDATIONS, OR DESCRIPTIONS CONTAINED HEREIN.  In no event will Siemens Westinghouse be responsible to the user in contract, in tort (including negligence), strict liability or otherwise for any special, indirect, incidental, or consequential damage or loss whatsoever, including but not limited to damage to or loss of use of equipment, plant, or power system; cost or capital; loss of profits or revenues; cost of replacement power; additional expenses in the use of existing power facilities; or claims against the user by its customers, resulting from use of the information, recommendations, or descriptions contained herein.

1.
REASON FOR advisory

The purpose of this Technical Advisory (TA) is to recommend replacement of the original W501F Row 3 turbine blades with blades of a new design.

During the 1996–1998 time period shroud lifting and cracking has been observed on several W501F Row 3 turbine blades.  The issue was attributed to high local temperatures and stresses in the Z-shroud area of the blade.

2.
Technical Recommendation

Replace all W501F Row 3 blades, manufactured from IN738 material with the new design blades.  The new design blades are made of CM247 material and have improved shroud configuration.

Replace the original design IN738 Row 3 turbine blades on W501F units during the following intervals:

· after 9,000 Equivalent Baseload Hours (EBH) - with DF-42 style combustor systems;

· after 16,000 EBH - with Dry Low NOx (DLN) combustor systems.

Figure 1.

W501F Row 3 Turbine Blade.

[image: image3.png]NN

NS

















OP0103

TA2000-014

© 2000 Siemens Westinghouse Power Corporation

             A Siemens Company

