Technical Data Sheet
ENRON 
June 5, 2000

Las Vegas-FC011400-2D-LS
GSU (2W) Transformer
 HU-Enron-2D-Lower Sound

RATING

Type
CP
Temp. rise
Cooling 
HV winding
LV winding
TV winding

Phases
3
Wind & Oil
Class
138
kV
13.8
kV

kV

Frequency
60
65
OA
84
MVA
84
MVA

MVA

Connection

65
FA
112
MVA
112
MVA

MVA

Standards
ANSI
65
FA
140
MVA
140
MVA

MVA

Off circuit taps:
+/-2 X 2.5% of 138 



PERFORMANCE DATA

Voltage
Impedance
Load Losses *
No Load
Sound L.
Auxiliary

kV
Base MVA
%
MVA
kW
% Volt.
kW
% Cur.
dB(A)
kW

138
84 H/X
9.0
84
161.0
100
57.0
0.17
70/72/73
6.5












* Based on 85°C winding temperature

DIELECTRIC TESTS

Applied to Ground
Over Voltage
Full Wave Impulse
Switching Impulse



kV


kV
H1, H2, H3
650/350  
kV


kV



kV


kV
X1, X2, X3
110
kV


kV



kV



Y1,Y2,Y3
110
kV

-
kV

DIMENSIONS (inches) AND WEIGHTS (lbs) **

Outline drawing

Core & coils weight 
158200

Total height
243
Untanking height
338
Tank & fittings weight
66600

Total length
   350
Transport height
190
Oil weight
90200

Total width
195
Transport length
   200
Total weight
315000

Height over cover
179
Transport width
143
Transport
200000

** Approximate, not for construction purpose

ADDITIONAL DATA

HV Bushings will have 650 KV BIL







