Operating Procedures Manual

date issued/revised
REPORTING OF
number

10-21-98

ABNORMAL OPERATIONS
80.413A

section

page


PIPELINE

Page 3 of 1


ABNORMAL OPERATION REPORT

Date of Abnormal Operation:
01-15-02

Date of Report:
01-17-02

PERSON SUBMITTING REPORT TO COMPANY REPORTING UNIT

Name:
Ted Lindblad

Job Title:
Mechanic

Business Telephone:
651-982-2127

LOCATION OF CONDITION

Region:
Minneapolis

Location:
North Branch, Mn.

Operating Company:
Northern Natural Gas Co.

Pipeline Name:

Number:


Station or Mile Post:


Compressor/Plant:
North Branch Compressor Station

State:
MN.

County/Parish:
Chisago

Section:
Township:35n
Range:21w
Survey:

Nearest Road or Street Address (where applicable):
Forest Blvd. 420th street

SIGNIFICANT DETAILS OF CONDITION

A BSD occurred because while routine maintenance work was being performed on a compressor (unit #3) the lead line suction valve for that unit was leaking enough in the closed position that when the compressor valve caps were removed, the gas detection system triggered a BSD.













PERSONNEL NOTIFIED

Control Center:
Bart in gas control was notified.

Supervision:


Other Location(s):














PERSONNEL AND EQUIPMENT DISPATCHED

Rick Watts, Jim Deming, Matt Rue, Mike Waldenburg, Randy Coe, and Ted Lindblad.









ACTIONS TAKEN

Jim Deming reset the plant to ready for a engine restart of unit #2.  Ted Lindblad, Rick Watts, Randy Coe, Matt Rue, and Mike Waldenburg replaced two compressor valves and caps and vented building, by opening up windows and doors.  Ted and Jim started #2 at 11:30 hrs.







ANALYSIS AND POSSIBLE ACTIONS TO PREVENT RECURRENCE

Work is going to be delayed (that portion of MP-2) until we can remove and replace that suction valve.  Somehow we have 3 suction valves in service with no grease zerts in them.  Contaminants in the system have evide3ntly collected on the ball / sealing area of that valve.







REVIEW PER OP 10.108

Date:-
01-17-01

Participants:
Team North Branch.

Comment(s):





