To: Kurt Anderson

From: Russ Leach

Date: 4/12/02

Subject: Another Comparison of Topas 1000 Meter to Turbine kWh Meter

Kurt:

This is a follow up on the last letter dated 4/4/02 where I checked the accuracy of the turbine meter in turbine #32A with a Topas 1000 meter. 

I put the Topas on turbine #89 on 4/4/02 at 6:06pm and let it run until 9:21am on 4/11/02. It still looks like the turbine meter is reading ok since I saw only about 1% difference between the two meters. At least it does not explain the very large difference between the turbine meters and the substation meters, which looks to be caused by lost data due to issues with the SCADA system.

When we started the test on 4/4/02 at 6:06pm, the reading from the turbine meter was:

2450242kWh Produced

5134kWh Consumed

When we ended the test on 4/11/02 at 9:21am, the reading from the turbine meter was:

2557272kWh Produced

5174kWh Consumed

The difference between these values is:

107030kWh Produced

40kWh consumed

Subtracting these two leaves 106990kWh for the period. This is the value that is compared to the Topas.

Going to the end of the table below and adding the energy together for the three phases gives 105702.5kWh produced for this time period as seen by the Topas.

As you can see the turbine read higher by 1.2%    

Like last time, the actual value is a little closer than this. I learned that when you download data from the Topas, the last data set is logging data and therefore is not downloaded. This caused us to be missing the last 10-minute average from the Topas. Since the turbine was running at full power when we downloaded, 10 minutes at 1500kW gives us 250kWh. Adding this to 105702.5kWh gives 105952.5kWh from the Topas. This gives a difference of .98%.

I hope this helps. Please call if you need any more information. 

Thank You

Russ Leach

Data from Topas 1000 Meter

Column 1 : Energy Phase1 [Wh]











Column 2 : Energy Phase2 [Wh]











Column 3 : Energy Phase3 [Wh]























Time
Column 39813
Column 1
Column 2
Column 3

04.04.2002 18:10:00
,000000
0
0
0

04.04.2002 18:20:00
,000000
2338,9
1557,24
2097,41

04.04.2002 18:30:00
,000000
6519,06
5014,15
6056,57

04.04.2002 18:40:00
,000000
11138,3
8957,27
10461,9

04.04.2002 18:50:00
,000000
15896,5
13042,1
14993,5

04.04.2002 19:00:00
,000000
21652,4
18140,6
20593,8

04.04.2002 19:10:00
,000000
23785,6
19510
22514,5

04.04.2002 19:20:00
,000000
29535,8
24599
28097,6

04.04.2002 19:30:00
,000000
34357,6
28773,4
32720,9

04.04.2002 19:40:00
,000000
44717,3
38625,7
42941,6

04.04.2002 19:50:00
,000000
54815,6
48283,8
52898,7

04.04.2002 20:00:00
,000000
66989,4
60096,4
64946,6

04.04.2002 20:10:00
,000000
78078,9
70830,6
75911,2

04.04.2002 20:20:00
,000000
88759,7
81204,9
86507,3

04.04.2002 20:30:00
,000000
99546,9
91704,6
97251,5

04.04.2002 20:40:00
,000000
110506
102377
108194

04.04.2002 20:50:00
,000000
120901
112461
118536

04.04.2002 21:00:00
,000000
132538
123816
130166

04.04.2002 21:10:00
,000000
151532
142749
149270

04.04.2002 21:20:00
,000000
174613
165896
172500

04.04.2002 21:30:00
,000000
209776
201342
207954

04.04.2002 21:40:00
,000000
253234
245276
251847

04.04.2002 21:50:00
,000000
295407
287946
294450

04.04.2002 22:00:00
,000000
341521
334616
341038

04.04.2002 22:10:00
,000000
383335
376922
383287

04.04.2002 22:20:00
,000000
421891
415910
422238

04.04.2002 22:30:00
,000000
461273
455722
462031

04.04.2002 22:40:00
,000000
502578
497491
503769

04.04.2002 22:50:00
,000000
552009
547522
553712

04.04.2002 23:00:00
,000000
608465
604878
610823

04.04.2002 23:10:00
,000000
660382
657603
663343

04.04.2002 23:20:00
,000000
707734
705611
711229

04.04.2002 23:30:00
,000000
743082
741317
746907

04.04.2002 23:40:00
,000000
770918
769406
775021

04.04.2002 23:50:00
,000000
803221
802148
807721

05.04.2002 00:00:00
,000000
842239
841796
847249

05.04.2002 00:10:00
,000000
882725
882888
888228

05.04.2002 00:20:00
,000000
914180
914706
920018

05.04.2002 00:30:00
,000000
936235
936977
942362

05.04.2002 00:40:00
,000000
958361
959362
964763

05.04.2002 00:50:00
,000000
987378
988806
994084

05.04.2002 01:00:00
,000000
1,02126e+06
1,02324e+06
1,02831e+06

05.04.2002 01:10:00
,000000
1,06331e+06
1,06607e+06
1,07084e+06

05.04.2002 01:20:00
,000000
1,098e+06
1,10138e+06
1,10588e+06

05.04.2002 01:30:00
,000000
1,12454e+06
1,12836e+06
1,13265e+06

05.04.2002 01:40:00
,000000
1,16426e+06
1,1688e+06
1,1728e+06

05.04.2002 01:50:00
,000000
1,19263e+06
1,19765e+06
1,20137e+06

05.04.2002 02:00:00
,000000
1,22145e+06
1,227e+06
1,23043e+06

05.04.2002 02:10:00
,000000
1,25035e+06
1,25639e+06
1,25952e+06

05.04.2002 02:20:00
,000000
1,27835e+06
1,28485e+06
1,28777e+06

05.04.2002 02:30:00
,000000
1,30858e+06
1,31559e+06
1,31832e+06

05.04.2002 02:40:00
,000000
1,34251e+06
1,35012e+06
1,35262e+06

05.04.2002 02:50:00
,000000
1,37654e+06
1,38483e+06
1,38704e+06

05.04.2002 03:00:00
,000000
1,41324e+06
1,42233e+06
1,42416e+06

05.04.2002 03:10:00
,000000
1,44217e+06
1,45184e+06
1,4534e+06

05.04.2002 03:20:00
,000000
1,46756e+06
1,47776e+06
1,47908e+06

05.04.2002 03:30:00
,000000
1,49335e+06
1,50406e+06
1,50517e+06

05.04.2002 03:40:00
,000000
1,51876e+06
1,52996e+06
1,53093e+06

05.04.2002 03:50:00
,000000
1,55014e+06
1,56194e+06
1,56274e+06

05.04.2002 04:00:00
,000000
1,58032e+06
1,59265e+06
1,59325e+06

05.04.2002 04:10:00
,000000
1,61385e+06
1,62673e+06
1,62713e+06

05.04.2002 04:20:00
,000000
1,64839e+06
1,66188e+06
1,66211e+06

05.04.2002 04:30:00
,000000
1,67004e+06
1,68386e+06
1,68403e+06

05.04.2002 04:40:00
,000000
1,71806e+06
1,73269e+06
1,73264e+06

05.04.2002 04:50:00
,000000
1,76266e+06
1,77807e+06
1,77784e+06

05.04.2002 05:00:00
,000000
1,81724e+06
1,83367e+06
1,83312e+06

05.04.2002 05:10:00
,000000
1,86871e+06
1,8861e+06
1,88526e+06

05.04.2002 05:20:00
,000000
1,91705e+06
1,93532e+06
1,93419e+06

05.04.2002 05:30:00
,000000
1,9639e+06
1,98299e+06
1,98156e+06

05.04.2002 05:40:00
,000000
2,02188e+06
2,04213e+06
2,04022e+06

05.04.2002 05:50:00
,000000
2,07899e+06
2,10036e+06
2,09793e+06

05.04.2002 06:00:00
,000000
2,14444e+06
2,16705e+06
2,16401e+06

05.04.2002 06:10:00
,000000
2,21653e+06
2,2405e+06
2,23678e+06

05.04.2002 06:20:00
,000000
2,29658e+06
2,32205e+06
2,31758e+06

05.04.2002 06:30:00
,000000
2,37861e+06
2,40566e+06
2,40037e+06

05.04.2002 06:40:00
,000000
2,46079e+06
2,48944e+06
2,48331e+06

05.04.2002 06:50:00
,000000
2,52826e+06
2,55808e+06
2,55142e+06

05.04.2002 07:00:00
,000000
2,53872e+06
2,56841e+06
2,56191e+06

05.04.2002 07:10:00
,000000
2,54239e+06
2,57201e+06
2,5656e+06

05.04.2002 07:20:00
,000000
2,55135e+06
2,58065e+06
2,57453e+06

05.04.2002 07:30:00
,000000
2,56293e+06
2,59201e+06
2,58614e+06

05.04.2002 07:40:00
,000000
2,57513e+06
2,60394e+06
2,59834e+06

05.04.2002 07:50:00
,000000
2,58909e+06
2,61769e+06
2,61236e+06

05.04.2002 08:00:00
,000000
2,59564e+06
2,6239e+06
2,61892e+06

05.04.2002 08:10:00
,000000
2,60407e+06
2,63206e+06
2,62737e+06

05.04.2002 08:20:00
,000000
2,6096e+06
2,63727e+06
2,6329e+06

05.04.2002 08:30:00
,000000
2,62519e+06
2,65273e+06
2,64858e+06

05.04.2002 08:40:00
,000000
2,63122e+06
2,65835e+06
2,65454e+06

05.04.2002 08:50:00
,000000
2,63662e+06
2,6633e+06
2,65986e+06

05.04.2002 09:00:00
,000000
2,644e+06
2,67021e+06
2,66716e+06

05.04.2002 09:10:00
,000000
2,65028e+06
2,67603e+06
2,67334e+06

05.04.2002 09:20:00
,000000
2,65742e+06
2,68268e+06
2,68033e+06

05.04.2002 09:30:00
,000000
2,66306e+06
2,68784e+06
2,6858e+06

05.04.2002 09:40:00
,000000
2,67664e+06
2,70115e+06
2,69936e+06

05.04.2002 09:50:00
,000000
2,7122e+06
2,73687e+06
2,73517e+06

05.04.2002 10:00:00
,000000
2,75543e+06
2,78047e+06
2,77874e+06

05.04.2002 10:10:00
,000000
2,82238e+06
2,84828e+06
2,84618e+06

05.04.2002 10:20:00
,000000
2,87262e+06
2,89912e+06
2,89685e+06

05.04.2002 10:30:00
,000000
2,91745e+06
2,94445e+06
2,94205e+06

05.04.2002 10:40:00
,000000
2,97418e+06
3,00193e+06
2,99926e+06

05.04.2002 10:50:00
,000000
3,02733e+06
3,05576e+06
3,05283e+06

05.04.2002 11:00:00
,000000
3,09321e+06
3,12263e+06
3,11922e+06

05.04.2002 11:10:00
,000000
3,15423e+06
3,1845e+06
3,18071e+06

05.04.2002 11:20:00
,000000
3,20377e+06
3,23461e+06
3,23061e+06

05.04.2002 11:30:00
,000000
3,24764e+06
3,2789e+06
3,27476e+06

05.04.2002 11:40:00
,000000
3,28418e+06
3,31566e+06
3,31153e+06

05.04.2002 11:50:00
,000000
3,30841e+06
3,33979e+06
3,33584e+06

05.04.2002 12:00:00
,000000
3,32365e+06
3,35475e+06
3,35104e+06

05.04.2002 12:10:00
,000000
3,34242e+06
3,37341e+06
3,3699e+06

05.04.2002 12:20:00
,000000
3,35654e+06
3,38733e+06
3,38408e+06

05.04.2002 12:30:00
,000000
3,37521e+06
3,4059e+06
3,40288e+06

05.04.2002 12:40:00
,000000
3,39956e+06
3,43023e+06
3,42738e+06

05.04.2002 12:50:00
,000000
3,42828e+06
3,45902e+06
3,4563e+06

05.04.2002 13:00:00
,000000
3,45674e+06
3,4875e+06
3,48489e+06

05.04.2002 13:10:00
,000000
3,482e+06
3,51274e+06
3,51031e+06

05.04.2002 13:20:00
,000000
3,49211e+06
3,52253e+06
3,52042e+06

05.04.2002 13:30:00
,000000
3,5137e+06
3,5441e+06
3,5422e+06

05.04.2002 13:40:00
,000000
3,55049e+06
3,58118e+06
3,57936e+06

05.04.2002 13:50:00
,000000
3,57758e+06
3,60836e+06
3,6067e+06

05.04.2002 14:00:00
,000000
3,60015e+06
3,63092e+06
3,62947e+06

05.04.2002 14:10:00
,000000
3,63278e+06
3,66372e+06
3,66242e+06

05.04.2002 14:20:00
,000000
3,65804e+06
3,68898e+06
3,6879e+06

05.04.2002 14:30:00
,000000
3,67987e+06
3,71066e+06
3,70989e+06

05.04.2002 14:40:00
,000000
3,70229e+06
3,73296e+06
3,7325e+06

05.04.2002 14:50:00
,000000
3,71635e+06
3,74671e+06
3,74665e+06

05.04.2002 15:00:00
,000000
3,72129e+06
3,75104e+06
3,75152e+06

05.04.2002 15:10:00
,000000
3,72687e+06
3,75638e+06
3,75714e+06

05.04.2002 15:20:00
,000000
3,7321e+06
3,76101e+06
3,76233e+06

05.04.2002 15:30:00
,000000
3,73232e+06
3,7609e+06
3,76249e+06

05.04.2002 15:40:00
,000000
3,73788e+06
3,76613e+06
3,76806e+06

05.04.2002 15:50:00
,000000
3,73974e+06
3,76728e+06
3,76978e+06

05.04.2002 16:00:00
,000000
3,7489e+06
3,77591e+06
3,77891e+06

05.04.2002 16:10:00
,000000
3,76162e+06
3,78821e+06
3,79171e+06

05.04.2002 16:20:00
,000000
3,776e+06
3,80218e+06
3,80618e+06

05.04.2002 16:30:00
,000000
3,78984e+06
3,8156e+06
3,82009e+06

05.04.2002 16:40:00
,000000
3,79949e+06
3,82469e+06
3,82975e+06

05.04.2002 16:50:00
,000000
3,81069e+06
3,83541e+06
3,84099e+06

05.04.2002 17:00:00
,000000
3,82474e+06
3,8491e+06
3,85513e+06

05.04.2002 17:10:00
,000000
3,8425e+06
3,86661e+06
3,87303e+06

05.04.2002 17:20:00
,000000
3,85873e+06
3,88255e+06
3,88937e+06

05.04.2002 17:30:00
,000000
3,8765e+06
3,90005e+06
3,90729e+06

05.04.2002 17:40:00
,000000
3,88575e+06
3,90881e+06
3,91654e+06

05.04.2002 17:50:00
,000000
3,8975e+06
3,9202e+06
3,92835e+06

05.04.2002 18:00:00
,000000
3,90708e+06
3,92934e+06
3,93795e+06

05.04.2002 18:10:00
,000000
3,9122e+06
3,9339e+06
3,94301e+06

05.04.2002 18:20:00
,000000
3,91697e+06
3,93807e+06
3,94771e+06

05.04.2002 18:30:00
,000000
3,92258e+06
3,94305e+06
3,95323e+06

05.04.2002 18:40:00
,000000
3,93255e+06
3,95255e+06
3,96322e+06

05.04.2002 18:50:00
,000000
3,93829e+06
3,95772e+06
3,96891e+06

05.04.2002 19:00:00
,000000
3,94548e+06
3,96435e+06
3,97608e+06

05.04.2002 19:10:00
,000000
3,94982e+06
3,9681e+06
3,98036e+06

05.04.2002 19:20:00
,000000
3,95731e+06
3,97509e+06
3,98786e+06

05.04.2002 19:30:00
,000000
3,96876e+06
3,98618e+06
3,99939e+06

05.04.2002 19:40:00
,000000
3,98059e+06
3,9977e+06
4,01129e+06

05.04.2002 19:50:00
,000000
3,99451e+06
4,01142e+06
4,02532e+06

05.04.2002 20:00:00
,000000
4,00418e+06
4,02081e+06
4,03501e+06

05.04.2002 20:10:00
,000000
4,01939e+06
4,03588e+06
4,05033e+06

05.04.2002 20:20:00
,000000
4,03163e+06
4,04788e+06
4,06266e+06

05.04.2002 20:30:00
,000000
4,04349e+06
4,05951e+06
4,07464e+06

05.04.2002 20:40:00
,000000
4,04967e+06
4,06535e+06
4,08088e+06

05.04.2002 20:50:00
,000000
4,06507e+06
4,08062e+06
4,09646e+06

05.04.2002 21:00:00
,000000
4,08e+06
4,09545e+06
4,11157e+06

05.04.2002 21:10:00
,000000
4,10113e+06
4,11660e+06
4,13295e+06

05.04.2002 21:20:00
,000000
4,11829e+06
4,13376e+06
4,15034e+06

05.04.2002 21:30:00
,000000
4,1433e+06
4,15893e+06
4,17566e+06

05.04.2002 21:40:00
,000000
4,17052e+06
4,18637e+06
4,20321e+06

05.04.2002 21:50:00
,000000
4,19958e+06
4,21566e+06
4,23259e+06

05.04.2002 22:00:00
,000000
4,22676e+06
4,243e+06
4,26004e+06

05.04.2002 22:10:00
,000000
4,25497e+06
4,2714e+06
4,28855e+06

05.04.2002 22:20:00
,000000
4,286e+06
4,30273e+06
4,31994e+06

05.04.2002 22:30:00
,000000
4,30962e+06
4,32645e+06
4,34383e+06

05.04.2002 22:40:00
,000000
4,32716e+06
4,34397e+06
4,36158e+06

05.04.2002 22:50:00
,000000
4,34762e+06
4,36446e+06
4,3823e+06

05.04.2002 23:00:00
,000000
4,37084e+06
4,3879e+06
4,40584e+06

05.04.2002 23:10:00
,000000
4,39832e+06
4,41569e+06
4,43368e+06

05.04.2002 23:20:00
,000000
4,44061e+06
4,45863e+06
4,47652e+06

05.04.2002 23:30:00
,000000
4,48714e+06
4,50598e+06
4,52366e+06

05.04.2002 23:40:00
,000000
4,53911e+06
4,55891e+06
4,57634e+06

05.04.2002 23:50:00
,000000
4,58711e+06
4,60776e+06
4,62501e+06

06.04.2002 00:00:00
,000000
4,62726e+06
4,64865e+06
4,66574e+06

06.04.2002 00:10:00
,000000
4,65622e+06
4,67808e+06
4,69508e+06

06.04.2002 00:20:00
,000000
4,69334e+06
4,71593e+06
4,73276e+06

06.04.2002 00:30:00
,000000
4,72697e+06
4,75021e+06
4,76686e+06

06.04.2002 00:40:00
,000000
4,76086e+06
4,78479e+06
4,80119e+06

06.04.2002 00:50:00
,000000
4,80614e+06
4,83102e+06
4,8471e+06

06.04.2002 01:00:00
,000000
4,84359e+06
4,86928e+06
4,88509e+06

06.04.2002 01:10:00
,000000
4,88081e+06
4,90718e+06
4,92285e+06

06.04.2002 01:20:00
,000000
4,91332e+06
4,94027e+06
4,95584e+06

06.04.2002 01:30:00
,000000
4,9491e+06
4,97671e+06
4,99213e+06

06.04.2002 01:40:00
,000000
4,99721e+06
5,02576e+06
5,04089e+06

06.04.2002 01:50:00
,000000
5,04783e+06
5,07732e+06
5,09212e+06

06.04.2002 02:00:00
,000000
5,08854e+06
5,11875e+06
5,13331e+06

06.04.2002 02:10:00
,000000
5,12779e+06
5,15863e+06
5,17299e+06

06.04.2002 02:20:00
,000000
5,16111e+06
5,19246e+06
5,20668e+06

06.04.2002 02:30:00
,000000
5,18108e+06
5,21265e+06
5,22688e+06

06.04.2002 02:40:00
,000000
5,21081e+06
5,24278e+06
5,25695e+06

06.04.2002 02:50:00
,000000
5,24176e+06
5,27419e+06
5,28826e+06

06.04.2002 03:00:00
,000000
5,28534e+06
5,31855e+06
5,33237e+06

06.04.2002 03:10:00
,000000
5,31978e+06
5,35365e+06
5,36728e+06

06.04.2002 03:20:00
,000000
5,35442e+06
5,389e+06
5,40246e+06

06.04.2002 03:30:00
,000000
5,38511e+06
5,42027e+06
5,43363e+06

06.04.2002 03:40:00
,000000
5,42794e+06
5,46389e+06
5,47709e+06

06.04.2002 03:50:00
,000000
5,46425e+06
5,50084e+06
5,51393e+06

06.04.2002 04:00:00
,000000
5,49521e+06
5,53231e+06
5,54532e+06

06.04.2002 04:10:00
,000000
5,52597e+06
5,56359e+06
5,57648e+06

06.04.2002 04:20:00
,000000
5,5571e+06
5,59528e+06
5,60801e+06

06.04.2002 04:30:00
,000000
5,59326e+06
5,63208e+06
5,64466e+06

06.04.2002 04:40:00
,000000
5,625e+06
5,6644e+06
5,67682e+06

06.04.2002 04:50:00
,000000
5,66792e+06
5,70819e+06
5,7203e+06

06.04.2002 05:00:00
,000000
5,71546e+06
5,75677e+06
5,76848e+06

06.04.2002 05:10:00
,000000
5,77561e+06
5,81825e+06
5,8294e+06

06.04.2002 05:20:00
,000000
5,83931e+06
5,88339e+06
5,8939e+06

06.04.2002 05:30:00
,000000
5,90267e+06
5,94816e+06
5,95806e+06

06.04.2002 05:40:00
,000000
5,97136e+06
6,01836e+06
6,02756e+06

06.04.2002 05:50:00
,000000
6,04136e+06
6,08993e+06
6,09835e+06

06.04.2002 06:00:00
,000000
6,11723e+06
6,16745e+06
6,17502e+06

06.04.2002 06:10:00
,000000
6,19103e+06
6,24294e+06
6,24963e+06

06.04.2002 06:20:00
,000000
6,2613e+06
6,31483e+06
6,32067e+06

06.04.2002 06:30:00
,000000
6,34035e+06
6,39569e+06
6,40055e+06

06.04.2002 06:40:00
,000000
6,42188e+06
6,47913e+06
6,48292e+06

06.04.2002 06:50:00
,000000
6,50312e+06
6,56228e+06
6,56505e+06

06.04.2002 07:00:00
,000000
6,58488e+06
6,64593e+06
6,64775e+06

06.04.2002 07:10:00
,000000
6,66699e+06
6,72994e+06
6,73086e+06

06.04.2002 07:20:00
,000000
6,74901e+06
6,81386e+06
6,81387e+06

06.04.2002 07:30:00
,000000
6,83116e+06
6,89786e+06
6,89694e+06

06.04.2002 07:40:00
,000000
6,91327e+06
6,98177e+06
6,97996e+06

06.04.2002 07:50:00
,000000
6,99541e+06
7,06569e+06
7,06297e+06

06.04.2002 08:00:00
,000000
7,07744e+06
7,14958e+06
7,14585e+06

06.04.2002 08:10:00
,000000
7,15957e+06
7,23358e+06
7,22887e+06

06.04.2002 08:20:00
,000000
7,24167e+06
7,31756e+06
7,31184e+06

06.04.2002 08:30:00
,000000
7,32374e+06
7,40149e+06
7,39476e+06

06.04.2002 08:40:00
,000000
7,4052e+06
7,48481e+06
7,47709e+06

06.04.2002 08:50:00
,000000
7,47321e+06
7,55443e+06
7,54592e+06

06.04.2002 09:00:00
,000000
7,55005e+06
7,63304e+06
7,62364e+06

06.04.2002 09:10:00
,000000
7,62296e+06
7,70755e+06
7,6974e+06

06.04.2002 09:20:00
,000000
7,69164e+06
7,7777e+06
7,76685e+06

06.04.2002 09:30:00
,000000
7,75296e+06
7,84033e+06
7,82891e+06

06.04.2002 09:40:00
,000000
7,82039e+06
7,90924e+06
7,89719e+06

06.04.2002 09:50:00
,000000
7,89527e+06
7,98574e+06
7,97294e+06

06.04.2002 10:00:00
,000000
7,9724e+06
8,06449e+06
8,05093e+06

06.04.2002 10:10:00
,000000
8,04895e+06
8,14272e+06
8,12834e+06

06.04.2002 10:20:00
,000000
8,12518e+06
8,22065e+06
8,20544e+06

06.04.2002 10:30:00
,000000
8,20008e+06
8,29722e+06
8,28119e+06

06.04.2002 10:40:00
,000000
8,26027e+06
8,35876e+06
8,34213e+06

06.04.2002 10:50:00
,000000
8,308e+06
8,40758e+06
8,3905e+06

06.04.2002 11:00:00
,000000
8,36799e+06
8,46887e+06
8,45127e+06

06.04.2002 11:10:00
,000000
8,41152e+06
8,51323e+06
8,49535e+06

06.04.2002 11:20:00
,000000
8,46124e+06
8,56393e+06
8,5457e+06

06.04.2002 11:30:00
,000000
8,51007e+06
8,61371e+06
8,59518e+06

06.04.2002 11:40:00
,000000
8,53111e+06
8,63512e+06
8,61651e+06

06.04.2002 11:50:00
,000000
8,58168e+06
8,68661e+06
8,66767e+06

06.04.2002 12:00:00
,000000
8,62857e+06
8,73429e+06
8,71516e+06

06.04.2002 12:10:00
,000000
8,66062e+06
8,76682e+06
8,74768e+06

06.04.2002 12:20:00
,000000
8,71317e+06
8,82031e+06
8,80094e+06

06.04.2002 12:30:00
,000000
8,74221e+06
8,84987e+06
8,83046e+06

06.04.2002 12:40:00
,000000
8,79949e+06
8,90828e+06
8,88853e+06

06.04.2002 12:50:00
,000000
8,84102e+06
8,95066e+06
8,9307e+06

06.04.2002 13:00:00
,000000
8,89405e+06
9,00474e+06
8,98444e+06

06.04.2002 13:10:00
,000000
8,94752e+06
9,05923e+06
9,03861e+06

06.04.2002 13:20:00
,000000
8,98762e+06
9,10008e+06
9,07927e+06

06.04.2002 13:30:00
,000000
9,01818e+06
9,13122e+06
9,11033e+06

06.04.2002 13:40:00
,000000
9,06111e+06
9,17498e+06
9,15388e+06

06.04.2002 13:50:00
,000000
9,10241e+06
9,21713e+06
9,19583e+06

06.04.2002 14:00:00
,000000
9,15749e+06
9,27323e+06
9,25166e+06

06.04.2002 14:10:00
,000000
9,1994e+06
9,31584e+06
9,29419e+06

06.04.2002 14:20:00
,000000
9,24809e+06
9,36539e+06
9,34357e+06

06.04.2002 14:30:00
,000000
9,28498e+06
9,40285e+06
9,381e+06

06.04.2002 14:40:00
,000000
9,31387e+06
9,43208e+06
9,4103e+06

06.04.2002 14:50:00
,000000
9,36749e+06
9,48651e+06
9,4646e+06

06.04.2002 15:00:00
,000000
9,40633e+06
9,52587e+06
9,504e+06

06.04.2002 15:10:00
,000000
9,45074e+06
9,57089e+06
9,54896e+06

06.04.2002 15:20:00
,000000
9,49469e+06
9,61535e+06
9,59342e+06

06.04.2002 15:30:00
,000000
9,53395e+06
9,65499e+06
9,63311e+06

06.04.2002 15:40:00
,000000
9,56406e+06
9,68534e+06
9,66357e+06

06.04.2002 15:50:00
,000000
9,60335e+06
9,72505e+06
9,70333e+06

06.04.2002 16:00:00
,000000
9,65488e+06
9,77728e+06
9,75549e+06

06.04.2002 16:10:00
,000000
9,69752e+06
9,82045e+06
9,79863e+06

06.04.2002 16:20:00
,000000
9,72566e+06
9,84884e+06
9,82714e+06

06.04.2002 16:30:00
,000000
9,75491e+06
9,87845e+06
9,85679e+06

06.04.2002 16:40:00
,000000
9,7968e+06
9,9209e+06
9,8992e+06

06.04.2002 16:50:00
,000000
9,83025e+06
9,95467e+06
9,93303e+06

06.04.2002 17:00:00
,000000
9,85555e+06
9,98015e+06
9,95865e+06

06.04.2002 17:10:00
,000000
9,88409e+06
1,0009e+07
9,98756e+06

06.04.2002 17:20:00
,000000
9,91708e+06
1,00423e+07
1,0021e+07

06.04.2002 17:30:00
,000000
9,94667e+06
1,00723e+07
1,0051e+07

06.04.2002 17:40:00
,000000
9,99242e+06
1,01187e+07
1,00973e+07

06.04.2002 17:50:00
,000000
1,00405e+07
1,01676e+07
1,0146e+07

06.04.2002 18:00:00
,000000
1,00843e+07
1,0212e+07
1,01903e+07

06.04.2002 18:10:00
,000000
1,01383e+07
1,0267e+07
1,02451e+07

06.04.2002 18:20:00
,000000
1,01713e+07
1,03005e+07
1,02786e+07

06.04.2002 18:30:00
,000000
1,02206e+07
1,03508e+07
1,03286e+07

06.04.2002 18:40:00
,000000
1,02902e+07
1,04217e+07
1,03989e+07

06.04.2002 18:50:00
,000000
1,03223e+07
1,04544e+07
1,04316e+07

06.04.2002 19:00:00
,000000
1,03584e+07
1,04912e+07
1,04681e+07

06.04.2002 19:10:00
,000000
1,04086e+07
1,05422e+07
1,05189e+07

06.04.2002 19:20:00
,000000
1,04654e+07
1,06001e+07
1,05764e+07

06.04.2002 19:30:00
,000000
1,05148e+07
1,06505e+07
1,06264e+07

06.04.2002 19:40:00
,000000
1,05828e+07
1,07199e+07
1,06952e+07

06.04.2002 19:50:00
,000000
1,06501e+07
1,07886e+07
1,07633e+07

06.04.2002 20:00:00
,000000
1,0707e+07
1,08466e+07
1,08209e+07

06.04.2002 20:10:00
,000000
1,07561e+07
1,08966e+07
1,08706e+07

06.04.2002 20:20:00
,000000
1,08217e+07
1,09634e+07
1,09368e+07

06.04.2002 20:30:00
,000000
1,08593e+07
1,10016e+07
1,09748e+07

06.04.2002 20:40:00
,000000
1,09041e+07
1,10472e+07
1,10202e+07

06.04.2002 20:50:00
,000000
1,0946e+07
1,109e+07
1,10626e+07

06.04.2002 21:00:00
,000000
1,1005e+07
1,11503e+07
1,11224e+07

06.04.2002 21:10:00
,000000
1,10831e+07
1,123e+07
1,12012e+07

06.04.2002 21:20:00
,000000
1,11651e+07
1,13139e+07
1,12841e+07

06.04.2002 21:30:00
,000000
1,12472e+07
1,13977e+07
1,13669e+07

06.04.2002 21:40:00
,000000
1,13293e+07
1,14817e+07
1,14499e+07

06.04.2002 21:50:00
,000000
1,14114e+07
1,15657e+07
1,15328e+07

06.04.2002 22:00:00
,000000
1,14936e+07
1,16497e+07
1,16157e+07

06.04.2002 22:10:00
,000000
1,15757e+07
1,17338e+07
1,16986e+07

06.04.2002 22:20:00
,000000
1,16578e+07
1,18178e+07
1,17815e+07

06.04.2002 22:30:00
,000000
1,17399e+07
1,19018e+07
1,18644e+07

06.04.2002 22:40:00
,000000
1,18219e+07
1,19858e+07
1,19473e+07

06.04.2002 22:50:00
,000000
1,1904e+07
1,20698e+07
1,20302e+07

06.04.2002 23:00:00
,000000
1,1986e+07
1,21538e+07
1,2113e+07

06.04.2002 23:10:00
,000000
1,20681e+07
1,22379e+07
1,21959e+07

06.04.2002 23:20:00
,000000
1,21501e+07
1,23219e+07
1,22787e+07

06.04.2002 23:30:00
,000000
1,22323e+07
1,2406e+07
1,23617e+07

06.04.2002 23:40:00
,000000
1,23142e+07
1,24899e+07
1,24445e+07

06.04.2002 23:50:00
,000000
1,23963e+07
1,25739e+07
1,25273e+07

07.04.2002 00:00:00
,000000
1,24785e+07
1,2658e+07
1,26104e+07

07.04.2002 00:10:00
,000000
1,25605e+07
1,27419e+07
1,26932e+07

07.04.2002 00:20:00
,000000
1,26426e+07
1,28259e+07
1,27761e+07

07.04.2002 00:30:00
,000000
1,27248e+07
1,291e+07
1,28591e+07

07.04.2002 00:40:00
,000000
1,28068e+07
1,29938e+07
1,29419e+07

07.04.2002 00:50:00
,000000
1,28875e+07
1,30763e+07
1,30234e+07

07.04.2002 01:00:00
,000000
1,29672e+07
1,31577e+07
1,31039e+07

07.04.2002 01:10:00
,000000
1,30495e+07
1,32417e+07
1,31869e+07

07.04.2002 01:20:00
,000000
1,31316e+07
1,33257e+07
1,32699e+07

07.04.2002 01:30:00
,000000
1,32129e+07
1,34086e+07
1,33519e+07

07.04.2002 01:40:00
,000000
1,32918e+07
1,34892e+07
1,34316e+07

07.04.2002 01:50:00
,000000
1,33581e+07
1,35568e+07
1,34985e+07

07.04.2002 02:00:00
,000000
1,34216e+07
1,36215e+07
1,35627e+07

07.04.2002 02:10:00
,000000
1,34699e+07
1,36707e+07
1,36116e+07

07.04.2002 02:20:00
,000000
1,35216e+07
1,37232e+07
1,36638e+07

07.04.2002 02:30:00
,000000
1,35623e+07
1,37645e+07
1,3705e+07

07.04.2002 02:40:00
,000000
1,35897e+07
1,3792e+07
1,37327e+07

07.04.2002 02:50:00
,000000
1,36077e+07
1,38101e+07
1,37509e+07

07.04.2002 03:00:00
,000000
1,36243e+07
1,38268e+07
1,37678e+07

07.04.2002 03:10:00
,000000
1,36432e+07
1,38459e+07
1,37869e+07

07.04.2002 03:20:00
,000000
1,36634e+07
1,38663e+07
1,38073e+07

07.04.2002 03:30:00
,000000
1,36932e+07
1,38966e+07
1,38374e+07

07.04.2002 03:40:00
,000000
1,37205e+07
1,39242e+07
1,38649e+07

07.04.2002 03:50:00
,000000
1,37445e+07
1,39486e+07
1,38892e+07

07.04.2002 04:00:00
,000000
1,37727e+07
1,39771e+07
1,39177e+07

07.04.2002 04:10:00
,000000
1,38172e+07
1,40224e+07
1,39626e+07

07.04.2002 04:20:00
,000000
1,38791e+07
1,40856e+07
1,40252e+07

07.04.2002 04:30:00
,000000
1,39508e+07
1,41589e+07
1,40976e+07

07.04.2002 04:40:00
,000000
1,40308e+07
1,42406e+07
1,41784e+07

07.04.2002 04:50:00
,000000
1,41127e+07
1,43243e+07
1,4261e+07

07.04.2002 05:00:00
,000000
1,41948e+07
1,44083e+07
1,4344e+07

07.04.2002 05:10:00
,000000
1,42769e+07
1,44923e+07
1,44269e+07

07.04.2002 05:20:00
,000000
1,4359e+07
1,45762e+07
1,45098e+07

07.04.2002 05:30:00
,000000
1,44412e+07
1,46602e+07
1,45927e+07

07.04.2002 05:40:00
,000000
1,45232e+07
1,47442e+07
1,46756e+07

07.04.2002 05:50:00
,000000
1,46052e+07
1,4828e+07
1,47584e+07

07.04.2002 06:00:00
,000000
1,46869e+07
1,49114e+07
1,48409e+07

07.04.2002 06:10:00
,000000
1,47327e+07
1,49578e+07
1,48872e+07

07.04.2002 06:20:00
,000000
1,47371e+07
1,49619e+07
1,48918e+07

07.04.2002 06:30:00
,000000
1,47382e+07
1,49628e+07
1,48929e+07

07.04.2002 06:40:00
,000000
1,47416e+07
1,49659e+07
1,48963e+07

07.04.2002 06:50:00
,000000
1,47527e+07
1,49769e+07
1,49075e+07

07.04.2002 07:00:00
,000000
1,47824e+07
1,50069e+07
1,49376e+07

07.04.2002 07:10:00
,000000
1,48464e+07
1,50721e+07
1,50023e+07

07.04.2002 07:20:00
,000000
1,49283e+07
1,51556e+07
1,5085e+07

07.04.2002 07:30:00
,000000
1,50103e+07
1,52393e+07
1,51679e+07

07.04.2002 07:40:00
,000000
1,50924e+07
1,53231e+07
1,52508e+07

07.04.2002 07:50:00
,000000
1,51745e+07
1,5407e+07
1,53338e+07

07.04.2002 08:00:00
,000000
1,52566e+07
1,54908e+07
1,54167e+07

07.04.2002 08:10:00
,000000
1,53388e+07
1,55748e+07
1,54998e+07

07.04.2002 08:20:00
,000000
1,5421e+07
1,56588e+07
1,55828e+07

07.04.2002 08:30:00
,000000
1,55032e+07
1,57428e+07
1,56659e+07

07.04.2002 08:40:00
,000000
1,55854e+07
1,58269e+07
1,57489e+07

07.04.2002 08:50:00
,000000
1,56676e+07
1,59109e+07
1,58319e+07

07.04.2002 09:00:00
,000000
1,57498e+07
1,5995e+07
1,59149e+07

07.04.2002 09:10:00
,000000
1,5832e+07
1,60791e+07
1,59979e+07

07.04.2002 09:20:00
,000000
1,59142e+07
1,61631e+07
1,60809e+07

07.04.2002 09:30:00
,000000
1,59962e+07
1,62471e+07
1,61637e+07

07.04.2002 09:40:00
,000000
1,60784e+07
1,63311e+07
1,62466e+07

07.04.2002 09:50:00
,000000
1,61605e+07
1,64152e+07
1,63295e+07

07.04.2002 10:00:00
,000000
1,62428e+07
1,64993e+07
1,64126e+07

07.04.2002 10:10:00
,000000
1,63249e+07
1,65833e+07
1,64956e+07

07.04.2002 10:20:00
,000000
1,64071e+07
1,66675e+07
1,65786e+07

07.04.2002 10:30:00
,000000
1,64884e+07
1,67507e+07
1,66607e+07

07.04.2002 10:40:00
,000000
1,65707e+07
1,68349e+07
1,67438e+07

07.04.2002 10:50:00
,000000
1,66528e+07
1,6919e+07
1,68268e+07

07.04.2002 11:00:00
,000000
1,67344e+07
1,70026e+07
1,69092e+07

07.04.2002 11:10:00
,000000
1,68166e+07
1,70867e+07
1,69922e+07

07.04.2002 11:20:00
,000000
1,68984e+07
1,71706e+07
1,70749e+07

07.04.2002 11:30:00
,000000
1,69806e+07
1,72547e+07
1,71579e+07

07.04.2002 11:40:00
,000000
1,7058e+07
1,7334e+07
1,72362e+07

07.04.2002 11:50:00
,000000
1,71383e+07
1,74163e+07
1,73173e+07

07.04.2002 12:00:00
,000000
1,72112e+07
1,74909e+07
1,73909e+07

07.04.2002 12:10:00
,000000
1,72909e+07
1,75724e+07
1,74714e+07

07.04.2002 12:20:00
,000000
1,73725e+07
1,76560e+07
1,75538e+07

07.04.2002 12:30:00
,000000
1,74548e+07
1,77403e+07
1,76368e+07

07.04.2002 12:40:00
,000000
1,75328e+07
1,78202e+07
1,77156e+07

07.04.2002 12:50:00
,000000
1,76148e+07
1,79041e+07
1,77984e+07

07.04.2002 13:00:00
,000000
1,76949e+07
1,7986e+07
1,78792e+07

07.04.2002 13:10:00
,000000
1,77655e+07
1,80583e+07
1,79505e+07

07.04.2002 13:20:00
,000000
1,78301e+07
1,81245e+07
1,80159e+07

07.04.2002 13:30:00
,000000
1,78915e+07
1,81872e+07
1,80779e+07

07.04.2002 13:40:00
,000000
1,79587e+07
1,82559e+07
1,81457e+07

07.04.2002 13:50:00
,000000
1,8013e+07
1,83114e+07
1,82005e+07

07.04.2002 14:00:00
,000000
1,80799e+07
1,83799e+07
1,82681e+07

07.04.2002 14:10:00
,000000
1,81333e+07
1,84345e+07
1,8322e+07

07.04.2002 14:20:00
,000000
1,81738e+07
1,84759e+07
1,8363e+07

07.04.2002 14:30:00
,000000
1,82123e+07
1,85152e+07
1,84019e+07

07.04.2002 14:40:00
,000000
1,82545e+07
1,85583e+07
1,84447e+07

07.04.2002 14:50:00
,000000
1,82953e+07
1,85998e+07
1,84859e+07

07.04.2002 15:00:00
,000000
1,83193e+07
1,86243e+07
1,85102e+07

07.04.2002 15:10:00
,000000
1,83361e+07
1,86414e+07
1,85273e+07

07.04.2002 15:20:00
,000000
1,84115e+07
1,87185e+07
1,86034e+07

07.04.2002 15:30:00
,000000
1,84735e+07
1,8782e+07
1,86661e+07

07.04.2002 15:40:00
,000000
1,85161e+07
1,88256e+07
1,87092e+07

07.04.2002 15:50:00
,000000
1,85577e+07
1,88682e+07
1,87512e+07

07.04.2002 16:00:00
,000000
1,85571e+07
1,88677e+07
1,87507e+07

07.04.2002 16:10:00
,000000
1,86232e+07
1,89352e+07
1,88175e+07

07.04.2002 16:20:00
,000000
1,87055e+07
1,90192e+07
1,89006e+07

07.04.2002 16:30:00
,000000
1,8766e+07
1,90809e+07
1,89618e+07

07.04.2002 16:40:00
,000000
1,87796e+07
1,90946e+07
1,89757e+07

07.04.2002 16:50:00
,000000
1,88302e+07
1,91462e+07
1,90269e+07

07.04.2002 17:00:00
,000000
1,88804e+07
1,91974e+07
1,90776e+07

07.04.2002 17:10:00
,000000
1,89049e+07
1,92221e+07
1,91024e+07

07.04.2002 17:20:00
,000000
1,89146e+07
1,92317e+07
1,91122e+07

07.04.2002 17:30:00
,000000
1,89194e+07
1,92362e+07
1,91171e+07

07.04.2002 17:40:00
,000000
1,89253e+07
1,92418e+07
1,91231e+07

07.04.2002 17:50:00
,000000
1,8927e+07
1,92433e+07
1,91249e+07

07.04.2002 18:00:00
,000000
1,89267e+07
1,9243e+07
1,91246e+07

07.04.2002 18:10:00
,000000
1,89264e+07
1,92428e+07
1,91243e+07

07.04.2002 18:20:00
,000000
1,89262e+07
1,92427e+07
1,91241e+07

07.04.2002 18:30:00
,000000
1,8926e+07
1,92426e+07
1,9124e+07

07.04.2002 18:40:00
,000000
1,89315e+07
1,92479e+07
1,91296e+07

07.04.2002 18:50:00
,000000
1,89363e+07
1,92524e+07
1,91343e+07

07.04.2002 19:00:00
,000000
1,89373e+07
1,92529e+07
1,91352e+07

07.04.2002 19:10:00
,000000
1,8937e+07
1,92526e+07
1,9135e+07

07.04.2002 19:20:00
,000000
1,89417e+07
1,92568e+07
1,91395e+07

07.04.2002 19:30:00
,000000
1,89509e+07
1,92657e+07
1,91487e+07

07.04.2002 19:40:00
,000000
1,89564e+07
1,92709e+07
1,91541e+07

07.04.2002 19:50:00
,000000
1,89683e+07
1,92826e+07
1,9166e+07

07.04.2002 20:00:00
,000000
1,89731e+07
1,92873e+07
1,91709e+07

07.04.2002 20:10:00
,000000
1,89781e+07
1,9292e+07
1,91758e+07

07.04.2002 20:20:00
,000000
1,89842e+07
1,92978e+07
1,9182e+07

07.04.2002 20:30:00
,000000
1,89861e+07
1,92994e+07
1,9184e+07

07.04.2002 20:40:00
,000000
1,89925e+07
1,93056e+07
1,91905e+07

07.04.2002 20:50:00
,000000
1,89966e+07
1,93095e+07
1,91947e+07

07.04.2002 21:00:00
,000000
1,89979e+07
1,93103e+07
1,91959e+07

07.04.2002 21:10:00
,000000
1,8999e+07
1,93109e+07
1,9197e+07

07.04.2002 21:20:00
,000000
1,90004e+07
1,93118e+07
1,91984e+07

07.04.2002 21:30:00
,000000
1,9002e+07
1,93128e+07
1,91999e+07

07.04.2002 21:40:00
,000000
1,90018e+07
1,93125e+07
1,91998e+07

07.04.2002 21:50:00
,000000
1,90031e+07
1,93134e+07
1,9201e+07

07.04.2002 22:00:00
,000000
1,90151e+07
1,93254e+07
1,92132e+07

07.04.2002 22:10:00
,000000
1,90421e+07
1,93526e+07
1,92404e+07

07.04.2002 22:20:00
,000000
1,90666e+07
1,93773e+07
1,92651e+07

07.04.2002 22:30:00
,000000
1,90943e+07
1,94053e+07
1,92931e+07

07.04.2002 22:40:00
,000000
1,91294e+07
1,94408e+07
1,93286e+07

07.04.2002 22:50:00
,000000
1,91599e+07
1,94716e+07
1,93592e+07

07.04.2002 23:00:00
,000000
1,91862e+07
1,94981e+07
1,93857e+07

07.04.2002 23:10:00
,000000
1,92187e+07
1,9531e+07
1,94185e+07

07.04.2002 23:20:00
,000000
1,92652e+07
1,95782e+07
1,94655e+07

07.04.2002 23:30:00
,000000
1,93131e+07
1,96268e+07
1,95139e+07

07.04.2002 23:40:00
,000000
1,93549e+07
1,96691e+07
1,95561e+07

07.04.2002 23:50:00
,000000
1,93863e+07
1,97008e+07
1,95878e+07

08.04.2002 00:00:00
,000000
1,94195e+07
1,97344e+07
1,96213e+07

08.04.2002 00:10:00
,000000
1,94454e+07
1,97606e+07
1,96474e+07

08.04.2002 00:20:00
,000000
1,94451e+07
1,97604e+07
1,96471e+07

08.04.2002 00:30:00
,000000
1,94882e+07
1,98042e+07
1,96907e+07

08.04.2002 00:40:00
,000000
1,95405e+07
1,98572e+07
1,97433e+07

08.04.2002 00:50:00
,000000
1,95925e+07
1,991e+07
1,97958e+07

08.04.2002 01:00:00
,000000
1,9646e+07
1,99643e+07
1,98497e+07

08.04.2002 01:10:00
,000000
1,96968e+07
2,00159e+07
1,9901e+07

08.04.2002 01:20:00
,000000
1,97561e+07
2,00763e+07
1,99608e+07

08.04.2002 01:30:00
,000000
1,98196e+07
2,01409e+07
2,00249e+07

08.04.2002 01:40:00
,000000
1,98858e+07
2,02083e+07
2,00917e+07

08.04.2002 01:50:00
,000000
1,99599e+07
2,02838e+07
2,01664e+07

08.04.2002 02:00:00
,000000
2,00263e+07
2,03514e+07
2,02335e+07

08.04.2002 02:10:00
,000000
2,00899e+07
2,04162e+07
2,02978e+07

08.04.2002 02:20:00
,000000
2,01587e+07
2,04862e+07
2,03672e+07

08.04.2002 02:30:00
,000000
2,02287e+07
2,05575e+07
2,04378e+07

08.04.2002 02:40:00
,000000
2,02945e+07
2,06245e+07
2,05043e+07

08.04.2002 02:50:00
,000000
2,03712e+07
2,07026e+07
2,05817e+07

08.04.2002 03:00:00
,000000
2,04525e+07
2,07855e+07
2,06638e+07

08.04.2002 03:10:00
,000000
2,0522e+07
2,08564e+07
2,07339e+07

08.04.2002 03:20:00
,000000
2,05746e+07
2,09101e+07
2,07872e+07

08.04.2002 03:30:00
,000000
2,0601e+07
2,0937e+07
2,08137e+07

08.04.2002 03:40:00
,000000
2,06338e+07
2,09705e+07
2,08469e+07

08.04.2002 03:50:00
,000000
2,0659e+07
2,09962e+07
2,08723e+07

08.04.2002 04:00:00
,000000
2,06774e+07
2,10148e+07
2,08909e+07

08.04.2002 04:10:00
,000000
2,0696e+07
2,10337e+07
2,09096e+07

08.04.2002 04:20:00
,000000
2,07292e+07
2,10676e+07
2,09432e+07

08.04.2002 04:30:00
,000000
2,07563e+07
2,10952e+07
2,09705e+07

08.04.2002 04:40:00
,000000
2,07853e+07
2,11246e+07
2,09998e+07

08.04.2002 04:50:00
,000000
2,08228e+07
2,11627e+07
2,10377e+07

08.04.2002 05:00:00
,000000
2,08427e+07
2,11827e+07
2,10577e+07

08.04.2002 05:10:00
,000000
2,08619e+07
2,1202e+07
2,1077e+07

08.04.2002 05:20:00
,000000
2,08841e+07
2,12243e+07
2,10994e+07

08.04.2002 05:30:00
,000000
2,09041e+07
2,12444e+07
2,11195e+07

08.04.2002 05:40:00
,000000
2,09298e+07
2,12701e+07
2,11454e+07

08.04.2002 05:50:00
,000000
2,09476e+07
2,12878e+07
2,11632e+07

08.04.2002 06:00:00
,000000
2,09618e+07
2,13018e+07
2,11775e+07

08.04.2002 06:10:00
,000000
2,0977e+07
2,13167e+07
2,11926e+07

08.04.2002 06:20:00
,000000
2,09907e+07
2,13302e+07
2,12063e+07

08.04.2002 06:30:00
,000000
2,10024e+07
2,13416e+07
2,1218e+07

08.04.2002 06:40:00
,000000
2,10173e+07
2,13564e+07
2,12329e+07

08.04.2002 06:50:00
,000000
2,10295e+07
2,13684e+07
2,12451e+07

08.04.2002 07:00:00
,000000
2,10414e+07
2,138e+07
2,12571e+07

08.04.2002 07:10:00
,000000
2,10534e+07
2,13918e+07
2,1269e+07

08.04.2002 07:20:00
,000000
2,10634e+07
2,14015e+07
2,12791e+07

08.04.2002 07:30:00
,000000
2,10732e+07
2,14109e+07
2,12888e+07

08.04.2002 07:40:00
,000000
2,10815e+07
2,14187e+07
2,12971e+07

08.04.2002 07:50:00
,000000
2,10888e+07
2,14254e+07
2,13043e+07

08.04.2002 08:00:00
,000000
2,10944e+07
2,14304e+07
2,13098e+07

08.04.2002 08:10:00
,000000
2,11009e+07
2,14363e+07
2,13162e+07

08.04.2002 08:20:00
,000000
2,11096e+07
2,14446e+07
2,1325e+07

08.04.2002 08:30:00
,000000
2,11227e+07
2,14572e+07
2,13381e+07

08.04.2002 08:40:00
,000000
2,11319e+07
2,14659e+07
2,13472e+07

08.04.2002 08:50:00
,000000
2,11395e+07
2,14731e+07
2,13548e+07

08.04.2002 09:00:00
,000000
2,11488e+07
2,14819e+07
2,13641e+07

08.04.2002 09:10:00
,000000
2,11571e+07
2,14897e+07
2,13723e+07

08.04.2002 09:20:00
,000000
2,11683e+07
2,15004e+07
2,13834e+07

08.04.2002 09:30:00
,000000
2,11749e+07
2,15064e+07
2,13898e+07

08.04.2002 09:40:00
,000000
2,118e+07
2,15108e+07
2,13947e+07

08.04.2002 09:50:00
,000000
2,11847e+07
2,15149e+07
2,13993e+07

08.04.2002 10:00:00
,000000
2,11859e+07
2,15158e+07
2,14004e+07

08.04.2002 10:10:00
,000000
2,11884e+07
2,15176e+07
2,14027e+07

08.04.2002 10:20:00
,000000
2,11899e+07
2,15189e+07
2,14042e+07

08.04.2002 10:30:00
,000000
2,11924e+07
2,1521e+07
2,14065e+07

08.04.2002 10:40:00
,000000
2,1198e+07
2,15261e+07
2,1412e+07

08.04.2002 10:50:00
,000000
2,12082e+07
2,15359e+07
2,14221e+07

08.04.2002 11:00:00
,000000
2,12195e+07
2,15465e+07
2,14333e+07

08.04.2002 11:10:00
,000000
2,12289e+07
2,15552e+07
2,14426e+07

08.04.2002 11:20:00
,000000
2,12406e+07
2,15664e+07
2,14542e+07

08.04.2002 11:30:00
,000000
2,12451e+07
2,15703e+07
2,14586e+07

08.04.2002 11:40:00
,000000
2,12516e+07
2,15762e+07
2,1465e+07

08.04.2002 11:50:00
,000000
2,12625e+07
2,15865e+07
2,14758e+07

08.04.2002 12:00:00
,000000
2,12819e+07
2,16057e+07
2,14953e+07

08.04.2002 12:10:00
,000000
2,1299e+07
2,16225e+07
2,15124e+07

08.04.2002 12:20:00
,000000
2,13173e+07
2,16405e+07
2,15308e+07

08.04.2002 12:30:00
,000000
2,13322e+07
2,16552e+07
2,15458e+07

08.04.2002 12:40:00
,000000
2,13663e+07
2,16895e+07
2,15802e+07

08.04.2002 12:50:00
,000000
2,14028e+07
2,17262e+07
2,16169e+07

08.04.2002 13:00:00
,000000
2,14307e+07
2,17543e+07
2,1645e+07

08.04.2002 13:10:00
,000000
2,14602e+07
2,17838e+07
2,16747e+07

08.04.2002 13:20:00
,000000
2,14859e+07
2,18096e+07
2,17006e+07

08.04.2002 13:30:00
,000000
2,15169e+07
2,18408e+07
2,17318e+07

08.04.2002 13:40:00
,000000
2,1546e+07
2,187e+07
2,17611e+07

08.04.2002 13:50:00
,000000
2,15792e+07
2,19033e+07
2,17944e+07

08.04.2002 14:00:00
,000000
2,16099e+07
2,19342e+07
2,18253e+07

08.04.2002 14:10:00
,000000
2,16399e+07
2,19645e+07
2,18556e+07

08.04.2002 14:20:00
,000000
2,1677e+07
2,20019e+07
2,18929e+07

08.04.2002 14:30:00
,000000
2,17074e+07
2,20326e+07
2,19235e+07

08.04.2002 14:40:00
,000000
2,17409e+07
2,20664e+07
2,19573e+07

08.04.2002 14:50:00
,000000
2,177e+07
2,20956e+07
2,19865e+07

08.04.2002 15:00:00
,000000
2,1802e+07
2,21278e+07
2,20187e+07

08.04.2002 15:10:00
,000000
2,18342e+07
2,21604e+07
2,20511e+07

08.04.2002 15:20:00
,000000
2,18624e+07
2,21889e+07
2,20796e+07

08.04.2002 15:30:00
,000000
2,18939e+07
2,22208e+07
2,21113e+07

08.04.2002 15:40:00
,000000
2,19255e+07
2,22526e+07
2,21431e+07

08.04.2002 15:50:00
,000000
2,19641e+07
2,22917e+07
2,21821e+07

08.04.2002 16:00:00
,000000
2,19815e+07
2,2309e+07
2,21994e+07

08.04.2002 16:10:00
,000000
2,20031e+07
2,23306e+07
2,22211e+07

08.04.2002 16:20:00
,000000
2,20327e+07
2,23605e+07
2,22509e+07

08.04.2002 16:30:00
,000000
2,2063e+07
2,2391e+07
2,22815e+07

08.04.2002 16:40:00
,000000
2,20904e+07
2,24185e+07
2,2309e+07

08.04.2002 16:50:00
,000000
2,21096e+07
2,24376e+07
2,23283e+07

08.04.2002 17:00:00
,000000
2,2138e+07
2,24661e+07
2,23569e+07

08.04.2002 17:10:00
,000000
2,2167e+07
2,24952e+07
2,23861e+07

08.04.2002 17:20:00
,000000
2,21876e+07
2,25158e+07
2,24069e+07

08.04.2002 17:30:00
,000000
2,22103e+07
2,25385e+07
2,24298e+07

08.04.2002 17:40:00
,000000
2,22336e+07
2,25619e+07
2,24532e+07

08.04.2002 17:50:00
,000000
2,22608e+07
2,25892e+07
2,24805e+07

08.04.2002 18:00:00
,000000
2,23045e+07
2,26335e+07
2,25246e+07

08.04.2002 18:10:00
,000000
2,23335e+07
2,26628e+07
2,25538e+07

08.04.2002 18:20:00
,000000
2,23641e+07
2,26937e+07
2,25847e+07

08.04.2002 18:30:00
,000000
2,23934e+07
2,27234e+07
2,26143e+07

08.04.2002 18:40:00
,000000
2,24111e+07
2,2741e+07
2,26321e+07

08.04.2002 18:50:00
,000000
2,24234e+07
2,27531e+07
2,26444e+07

08.04.2002 19:00:00
,000000
2,24305e+07
2,27597e+07
2,26514e+07

08.04.2002 19:10:00
,000000
2,2439e+07
2,2768e+07
2,266e+07

08.04.2002 19:20:00
,000000
2,24435e+07
2,27721e+07
2,26645e+07

08.04.2002 19:30:00
,000000
2,24475e+07
2,27756e+07
2,26684e+07

08.04.2002 19:40:00
,000000
2,2453e+07
2,27806e+07
2,26739e+07

08.04.2002 19:50:00
,000000
2,24577e+07
2,27849e+07
2,26785e+07

08.04.2002 20:00:00
,000000
2,24623e+07
2,2789e+07
2,26831e+07

08.04.2002 20:10:00
,000000
2,24648e+07
2,2791e+07
2,26855e+07

08.04.2002 20:20:00
,000000
2,24668e+07
2,27925e+07
2,26875e+07

08.04.2002 20:30:00
,000000
2,24704e+07
2,27956e+07
2,26911e+07

08.04.2002 20:40:00
,000000
2,24714e+07
2,27961e+07
2,26921e+07

08.04.2002 20:50:00
,000000
2,24735e+07
2,27978e+07
2,26942e+07

08.04.2002 21:00:00
,000000
2,24799e+07
2,28038e+07
2,27006e+07

08.04.2002 21:10:00
,000000
2,24885e+07
2,28123e+07
2,27094e+07

08.04.2002 21:20:00
,000000
2,24945e+07
2,28179e+07
2,27154e+07

08.04.2002 21:30:00
,000000
2,24948e+07
2,28178e+07
2,27157e+07

08.04.2002 21:40:00
,000000
2,24952e+07
2,28178e+07
2,27161e+07

08.04.2002 21:50:00
,000000
2,24953e+07
2,28175e+07
2,27162e+07

08.04.2002 22:00:00
,000000
2,24979e+07
2,28198e+07
2,27188e+07

08.04.2002 22:10:00
,000000
2,25022e+07
2,28239e+07
2,27232e+07

08.04.2002 22:20:00
,000000
2,25101e+07
2,28316e+07
2,27312e+07

08.04.2002 22:30:00
,000000
2,25177e+07
2,28389e+07
2,27388e+07

08.04.2002 22:40:00
,000000
2,25269e+07
2,2848e+07
2,27482e+07

08.04.2002 22:50:00
,000000
2,2536e+07
2,2857e+07
2,27574e+07

08.04.2002 23:00:00
,000000
2,25447e+07
2,28655e+07
2,27662e+07

08.04.2002 23:10:00
,000000
2,25533e+07
2,28738e+07
2,27748e+07

08.04.2002 23:20:00
,000000
2,25662e+07
2,28868e+07
2,27878e+07

08.04.2002 23:30:00
,000000
2,2583e+07
2,29036e+07
2,28048e+07

08.04.2002 23:40:00
,000000
2,26e+07
2,29207e+07
2,28219e+07

08.04.2002 23:50:00
,000000
2,26126e+07
2,29332e+07
2,28346e+07

09.04.2002 00:00:00
,000000
2,26288e+07
2,29496e+07
2,28509e+07

09.04.2002 00:10:00
,000000
2,26573e+07
2,29784e+07
2,28796e+07

09.04.2002 00:20:00
,000000
2,26778e+07
2,2999e+07
2,29002e+07

09.04.2002 00:30:00
,000000
2,26913e+07
2,30126e+07
2,29138e+07

09.04.2002 00:40:00
,000000
2,2703e+07
2,30242e+07
2,29256e+07

09.04.2002 00:50:00
,000000
2,27163e+07
2,30375e+07
2,29389e+07

09.04.2002 01:00:00
,000000
2,27259e+07
2,3047e+07
2,29486e+07

09.04.2002 01:10:00
,000000
2,27351e+07
2,30562e+07
2,29579e+07

09.04.2002 01:20:00
,000000
2,2746e+07
2,3067e+07
2,29688e+07

09.04.2002 01:30:00
,000000
2,27601e+07
2,30813e+07
2,29831e+07

09.04.2002 01:40:00
,000000
2,27778e+07
2,30991e+07
2,3001e+07

09.04.2002 01:50:00
,000000
2,27938e+07
2,31152e+07
2,30171e+07

09.04.2002 02:00:00
,000000
2,28087e+07
2,31302e+07
2,30322e+07

09.04.2002 02:10:00
,000000
2,28234e+07
2,3145e+07
2,30469e+07

09.04.2002 02:20:00
,000000
2,28398e+07
2,31614e+07
2,30634e+07

09.04.2002 02:30:00
,000000
2,28514e+07
2,31729e+07
2,3075e+07

09.04.2002 02:40:00
,000000
2,28621e+07
2,31835e+07
2,30858e+07

09.04.2002 02:50:00
,000000
2,28757e+07
2,31971e+07
2,30996e+07

09.04.2002 03:00:00
,000000
2,28984e+07
2,32201e+07
2,31226e+07

09.04.2002 03:10:00
,000000
2,29358e+07
2,3258e+07
2,31605e+07

09.04.2002 03:20:00
,000000
2,29631e+07
2,32858e+07
2,31882e+07

09.04.2002 03:30:00
,000000
2,2989e+07
2,3312e+07
2,32144e+07

09.04.2002 03:40:00
,000000
2,30216e+07
2,33452e+07
2,32475e+07

09.04.2002 03:50:00
,000000
2,30662e+07
2,33906e+07
2,32927e+07

09.04.2002 04:00:00
,000000
2,311e+07
2,34352e+07
2,33372e+07

09.04.2002 04:10:00
,000000
2,31454e+07
2,34711e+07
2,3373e+07

09.04.2002 04:20:00
,000000
2,3171e+07
2,3497e+07
2,3399e+07

09.04.2002 04:30:00
,000000
2,31937e+07
2,352e+07
2,34221e+07

09.04.2002 04:40:00
,000000
2,32133e+07
2,35397e+07
2,3442e+07

09.04.2002 04:50:00
,000000
2,32274e+07
2,35538e+07
2,34563e+07

09.04.2002 05:00:00
,000000
2,32408e+07
2,35672e+07
2,34699e+07

09.04.2002 05:10:00
,000000
2,32527e+07
2,35791e+07
2,34821e+07

09.04.2002 05:20:00
,000000
2,32673e+07
2,35937e+07
2,34968e+07

09.04.2002 05:30:00
,000000
2,32893e+07
2,3616e+07
2,35192e+07

09.04.2002 05:40:00
,000000
2,33127e+07
2,36397e+07
2,35429e+07

09.04.2002 05:50:00
,000000
2,33369e+07
2,36642e+07
2,35674e+07

09.04.2002 06:00:00
,000000
2,33657e+07
2,36933e+07
2,35965e+07

09.04.2002 06:10:00
,000000
2,33998e+07
2,37277e+07
2,3631e+07

09.04.2002 06:20:00
,000000
2,34363e+07
2,37647e+07
2,3668e+07

09.04.2002 06:30:00
,000000
2,34712e+07
2,38001e+07
2,37034e+07

09.04.2002 06:40:00
,000000
2,35048e+07
2,3834e+07
2,37373e+07

09.04.2002 06:50:00
,000000
2,35396e+07
2,38692e+07
2,37725e+07

09.04.2002 07:00:00
,000000
2,35737e+07
2,39037e+07
2,3807e+07

09.04.2002 07:10:00
,000000
2,3605e+07
2,39351e+07
2,38386e+07

09.04.2002 07:20:00
,000000
2,36273e+07
2,39574e+07
2,38612e+07

09.04.2002 07:30:00
,000000
2,36478e+07
2,39779e+07
2,38819e+07

09.04.2002 07:40:00
,000000
2,36636e+07
2,39937e+07
2,3898e+07

09.04.2002 07:50:00
,000000
2,36768e+07
2,40067e+07
2,39113e+07

09.04.2002 08:00:00
,000000
2,36942e+07
2,4024e+07
2,39289e+07

09.04.2002 08:10:00
,000000
2,3708e+07
2,40376e+07
2,39428e+07

09.04.2002 08:20:00
,000000
2,37201e+07
2,40495e+07
2,3955e+07

09.04.2002 08:30:00
,000000
2,37353e+07
2,40646e+07
2,39703e+07

09.04.2002 08:40:00
,000000
2,37491e+07
2,40781e+07
2,39842e+07

09.04.2002 08:50:00
,000000
2,37669e+07
2,40958e+07
2,40021e+07

09.04.2002 09:00:00
,000000
2,37871e+07
2,4116e+07
2,40225e+07

09.04.2002 09:10:00
,000000
2,38007e+07
2,41294e+07
2,40363e+07

09.04.2002 09:20:00
,000000
2,38136e+07
2,4142e+07
2,40493e+07

09.04.2002 09:30:00
,000000
2,3828e+07
2,41562e+07
2,40638e+07

09.04.2002 09:40:00
,000000
2,3841e+07
2,41689e+07
2,40769e+07

09.04.2002 09:50:00
,000000
2,38498e+07
2,41775e+07
2,40859e+07

09.04.2002 10:00:00
,000000
2,38658e+07
2,41934e+07
2,4102e+07

09.04.2002 10:10:00
,000000
2,38738e+07
2,4201e+07
2,411e+07

09.04.2002 10:20:00
,000000
2,38782e+07
2,4205e+07
2,41145e+07

09.04.2002 10:30:00
,000000
2,38841e+07
2,42104e+07
2,41203e+07

09.04.2002 10:40:00
,000000
2,38904e+07
2,42163e+07
2,41267e+07

09.04.2002 10:50:00
,000000
2,3894e+07
2,42194e+07
2,41303e+07

09.04.2002 11:00:00
,000000
2,39009e+07
2,42259e+07
2,41372e+07

09.04.2002 11:10:00
,000000
2,39074e+07
2,42319e+07
2,41437e+07

09.04.2002 11:20:00
,000000
2,39131e+07
2,42371e+07
2,41494e+07

09.04.2002 11:30:00
,000000
2,39193e+07
2,42428e+07
2,41555e+07

09.04.2002 11:40:00
,000000
2,39219e+07
2,42448e+07
2,41582e+07

09.04.2002 11:50:00
,000000
2,39266e+07
2,42491e+07
2,41629e+07

09.04.2002 12:00:00
,000000
2,39305e+07
2,42525e+07
2,41668e+07

09.04.2002 12:10:00
,000000
2,39382e+07
2,42597e+07
2,41745e+07

09.04.2002 12:20:00
,000000
2,39517e+07
2,4273e+07
2,41882e+07

09.04.2002 12:30:00
,000000
2,39617e+07
2,42826e+07
2,41982e+07

09.04.2002 12:40:00
,000000
2,39679e+07
2,42884e+07
2,42045e+07

09.04.2002 12:50:00
,000000
2,39724e+07
2,42924e+07
2,42088e+07

09.04.2002 13:00:00
,000000
2,39784e+07
2,42979e+07
2,42148e+07

09.04.2002 13:10:00
,000000
2,39811e+07
2,43001e+07
2,42174e+07

09.04.2002 13:20:00
,000000
2,39877e+07
2,43063e+07
2,42241e+07

09.04.2002 13:30:00
,000000
2,39927e+07
2,43107e+07
2,42289e+07

09.04.2002 13:40:00
,000000
2,40011e+07
2,43188e+07
2,42374e+07

09.04.2002 13:50:00
,000000
2,40066e+07
2,43238e+07
2,42429e+07

09.04.2002 14:00:00
,000000
2,40079e+07
2,43245e+07
2,42441e+07

09.04.2002 14:10:00
,000000
2,40092e+07
2,43254e+07
2,42453e+07

09.04.2002 14:20:00
,000000
2,40092e+07
2,43252e+07
2,42453e+07

09.04.2002 14:30:00
,000000
2,40106e+07
2,4326e+07
2,42466e+07

09.04.2002 14:40:00
,000000
2,40124e+07
2,43272e+07
2,42484e+07

09.04.2002 14:50:00
,000000
2,40125e+07
2,4327e+07
2,42485e+07

09.04.2002 15:00:00
,000000
2,40128e+07
2,43271e+07
2,42487e+07

09.04.2002 15:10:00
,000000
2,40137e+07
2,43277e+07
2,42496e+07

09.04.2002 15:20:00
,000000
2,40191e+07
2,43326e+07
2,42549e+07

09.04.2002 15:30:00
,000000
2,40214e+07
2,43342e+07
2,4257e+07

09.04.2002 15:40:00
,000000
2,40246e+07
2,43369e+07
2,42601e+07

09.04.2002 15:50:00
,000000
2,40275e+07
2,43392e+07
2,42629e+07

09.04.2002 16:00:00
,000000
2,40293e+07
2,43406e+07
2,42646e+07

09.04.2002 16:10:00
,000000
2,40319e+07
2,43428e+07
2,42672e+07

09.04.2002 16:20:00
,000000
2,40335e+07
2,4344e+07
2,42688e+07

09.04.2002 16:30:00
,000000
2,40344e+07
2,43447e+07
2,42696e+07

09.04.2002 16:40:00
,000000
2,40361e+07
2,43461e+07
2,42712e+07

09.04.2002 16:50:00
,000000
2,40375e+07
2,43471e+07
2,42725e+07

09.04.2002 17:00:00
,000000
2,40403e+07
2,43494e+07
2,42752e+07

09.04.2002 17:10:00
,000000
2,40431e+07
2,43517e+07
2,42779e+07

09.04.2002 17:20:00
,000000
2,40444e+07
2,43526e+07
2,42791e+07

09.04.2002 17:30:00
,000000
2,40476e+07
2,43554e+07
2,42823e+07

09.04.2002 17:40:00
,000000
2,40517e+07
2,43591e+07
2,42864e+07

09.04.2002 17:50:00
,000000
2,40524e+07
2,43592e+07
2,42869e+07

09.04.2002 18:00:00
,000000
2,40525e+07
2,43592e+07
2,42871e+07

09.04.2002 18:10:00
,000000
2,40547e+07
2,43609e+07
2,42892e+07

09.04.2002 18:20:00
,000000
2,40574e+07
2,43629e+07
2,42918e+07

09.04.2002 18:30:00
,000000
2,40594e+07
2,43642e+07
2,42937e+07

09.04.2002 18:40:00
,000000
2,40631e+07
2,43674e+07
2,42975e+07

09.04.2002 18:50:00
,000000
2,40693e+07
2,43731e+07
2,43037e+07

09.04.2002 19:00:00
,000000
2,40732e+07
2,43765e+07
2,43075e+07

09.04.2002 19:10:00
,000000
2,40792e+07
2,43821e+07
2,43136e+07

09.04.2002 19:20:00
,000000
2,4081e+07
2,43833e+07
2,43153e+07

09.04.2002 19:30:00
,000000
2,40837e+07
2,43855e+07
2,43179e+07

09.04.2002 19:40:00
,000000
2,40878e+07
2,43891e+07
2,4322e+07

09.04.2002 19:50:00
,000000
2,40918e+07
2,43925e+07
2,43259e+07

09.04.2002 20:00:00
,000000
2,40952e+07
2,43954e+07
2,43292e+07

09.04.2002 20:10:00
,000000
2,41006e+07
2,44004e+07
2,43346e+07

09.04.2002 20:20:00
,000000
2,41071e+07
2,44066e+07
2,4341e+07

09.04.2002 20:30:00
,000000
2,41136e+07
2,44127e+07
2,43475e+07

09.04.2002 20:40:00
,000000
2,41202e+07
2,4419e+07
2,43541e+07

09.04.2002 20:50:00
,000000
2,41274e+07
2,44259e+07
2,43613e+07

09.04.2002 21:00:00
,000000
2,41347e+07
2,44328e+07
2,43685e+07

09.04.2002 21:10:00
,000000
2,41437e+07
2,44415e+07
2,43775e+07

09.04.2002 21:20:00
,000000
2,41546e+07
2,44521e+07
2,43884e+07

09.04.2002 21:30:00
,000000
2,41705e+07
2,44679e+07
2,44045e+07

09.04.2002 21:40:00
,000000
2,41877e+07
2,44849e+07
2,44218e+07

09.04.2002 21:50:00
,000000
2,42064e+07
2,45037e+07
2,44407e+07

09.04.2002 22:00:00
,000000
2,42208e+07
2,45181e+07
2,44553e+07

09.04.2002 22:10:00
,000000
2,4231e+07
2,45282e+07
2,44656e+07

09.04.2002 22:20:00
,000000
2,42402e+07
2,45373e+07
2,44749e+07

09.04.2002 22:30:00
,000000
2,42492e+07
2,45462e+07
2,4484e+07

09.04.2002 22:40:00
,000000
2,42597e+07
2,45566e+07
2,44946e+07

09.04.2002 22:50:00
,000000
2,427e+07
2,45668e+07
2,4505e+07

09.04.2002 23:00:00
,000000
2,42814e+07
2,45782e+07
2,45166e+07

09.04.2002 23:10:00
,000000
2,42941e+07
2,4591e+07
2,45295e+07

09.04.2002 23:20:00
,000000
2,43064e+07
2,46033e+07
2,45419e+07

09.04.2002 23:30:00
,000000
2,43239e+07
2,4621e+07
2,45598e+07

09.04.2002 23:40:00
,000000
2,43383e+07
2,46355e+07
2,45744e+07

09.04.2002 23:50:00
,000000
2,43549e+07
2,46522e+07
2,45912e+07

10.04.2002 00:00:00
,000000
2,43719e+07
2,46694e+07
2,46085e+07

10.04.2002 00:10:00
,000000
2,43883e+07
2,46861e+07
2,46252e+07

10.04.2002 00:20:00
,000000
2,44066e+07
2,47047e+07
2,46438e+07

10.04.2002 00:30:00
,000000
2,44379e+07
2,47365e+07
2,46754e+07

10.04.2002 00:40:00
,000000
2,44644e+07
2,47636e+07
2,47022e+07

10.04.2002 00:50:00
,000000
2,4487e+07
2,47867e+07
2,47252e+07

10.04.2002 01:00:00
,000000
2,45099e+07
2,481e+07
2,47485e+07

10.04.2002 01:10:00
,000000
2,45349e+07
2,48354e+07
2,47738e+07

10.04.2002 01:20:00
,000000
2,45706e+07
2,48719e+07
2,48101e+07

10.04.2002 01:30:00
,000000
2,46213e+07
2,49236e+07
2,48615e+07

10.04.2002 01:40:00
,000000
2,46668e+07
2,497e+07
2,49077e+07

10.04.2002 01:50:00
,000000
2,47083e+07
2,50123e+07
2,49498e+07

10.04.2002 02:00:00
,000000
2,47564e+07
2,50613e+07
2,49986e+07

10.04.2002 02:10:00
,000000
2,48055e+07
2,51113e+07
2,50484e+07

10.04.2002 02:20:00
,000000
2,48624e+07
2,51694e+07
2,51062e+07

10.04.2002 02:30:00
,000000
2,49259e+07
2,52342e+07
2,51707e+07

10.04.2002 02:40:00
,000000
2,49761e+07
2,52853e+07
2,52216e+07

10.04.2002 02:50:00
,000000
2,5021e+07
2,53311e+07
2,52672e+07

10.04.2002 03:00:00
,000000
2,50698e+07
2,53808e+07
2,53166e+07

10.04.2002 03:10:00
,000000
2,51176e+07
2,54296e+07
2,53652e+07

10.04.2002 03:20:00
,000000
2,51659e+07
2,54789e+07
2,54142e+07

10.04.2002 03:30:00
,000000
2,5219e+07
2,55331e+07
2,54681e+07

10.04.2002 03:40:00
,000000
2,52651e+07
2,55803e+07
2,5515e+07

10.04.2002 03:50:00
,000000
2,5307e+07
2,5623e+07
2,55575e+07

10.04.2002 04:00:00
,000000
2,53395e+07
2,56562e+07
2,55905e+07

10.04.2002 04:10:00
,000000
2,53627e+07
2,56798e+07
2,56141e+07

10.04.2002 04:20:00
,000000
2,53977e+07
2,57157e+07
2,56497e+07

10.04.2002 04:30:00
,000000
2,54279e+07
2,57466e+07
2,56803e+07

10.04.2002 04:40:00
,000000
2,54633e+07
2,57829e+07
2,57162e+07

10.04.2002 04:50:00
,000000
2,55132e+07
2,5834e+07
2,57669e+07

10.04.2002 05:00:00
,000000
2,55811e+07
2,59035e+07
2,58356e+07

10.04.2002 05:10:00
,000000
2,56623e+07
2,59864e+07
2,59176e+07

10.04.2002 05:20:00
,000000
2,57426e+07
2,60684e+07
2,59988e+07

10.04.2002 05:30:00
,000000
2,58242e+07
2,61518e+07
2,60813e+07

10.04.2002 05:40:00
,000000
2,59055e+07
2,62348e+07
2,61635e+07

10.04.2002 05:50:00
,000000
2,59872e+07
2,63183e+07
2,62461e+07

10.04.2002 06:00:00
,000000
2,60667e+07
2,63993e+07
2,63265e+07

10.04.2002 06:10:00
,000000
2,61396e+07
2,64737e+07
2,64002e+07

10.04.2002 06:20:00
,000000
2,62077e+07
2,6543e+07
2,64691e+07

10.04.2002 06:30:00
,000000
2,62432e+07
2,65791e+07
2,6505e+07

10.04.2002 06:40:00
,000000
2,62825e+07
2,6619e+07
2,65447e+07

10.04.2002 06:50:00
,000000
2,63162e+07
2,66531e+07
2,65787e+07

10.04.2002 07:00:00
,000000
2,63477e+07
2,66851e+07
2,66106e+07

10.04.2002 07:10:00
,000000
2,63936e+07
2,67317e+07
2,6657e+07

10.04.2002 07:20:00
,000000
2,64479e+07
2,67871e+07
2,6712e+07

10.04.2002 07:30:00
,000000
2,65289e+07
2,68696e+07
2,67938e+07

10.04.2002 07:40:00
,000000
2,66111e+07
2,69534e+07
2,68768e+07

10.04.2002 07:50:00
,000000
2,66932e+07
2,70371e+07
2,69598e+07

10.04.2002 08:00:00
,000000
2,67756e+07
2,71211e+07
2,7043e+07

10.04.2002 08:10:00
,000000
2,68578e+07
2,72049e+07
2,7126e+07

10.04.2002 08:20:00
,000000
2,69401e+07
2,72888e+07
2,7209e+07

10.04.2002 08:30:00
,000000
2,70224e+07
2,73725e+07
2,7292e+07

10.04.2002 08:40:00
,000000
2,71046e+07
2,74563e+07
2,73750e+07

10.04.2002 08:50:00
,000000
2,7187e+07
2,75402e+07
2,74581e+07

10.04.2002 09:00:00
,000000
2,72691e+07
2,76238e+07
2,7541e+07

10.04.2002 09:10:00
,000000
2,73482e+07
2,77043e+07
2,76208e+07

10.04.2002 09:20:00
,000000
2,74145e+07
2,77717e+07
2,76878e+07

10.04.2002 09:30:00
,000000
2,74857e+07
2,78441e+07
2,77597e+07

10.04.2002 09:40:00
,000000
2,75479e+07
2,79072e+07
2,78225e+07

10.04.2002 09:50:00
,000000
2,75972e+07
2,79573e+07
2,78723e+07

10.04.2002 10:00:00
,000000
2,76289e+07
2,79891e+07
2,79041e+07

10.04.2002 10:10:00
,000000
2,76522e+07
2,80125e+07
2,79276e+07

10.04.2002 10:20:00
,000000
2,76799e+07
2,80402e+07
2,79554e+07

10.04.2002 10:30:00
,000000
2,77068e+07
2,80672e+07
2,79825e+07

10.04.2002 10:40:00
,000000
2,77255e+07
2,80856e+07
2,80012e+07

10.04.2002 10:50:00
,000000
2,77516e+07
2,81118e+07
2,80275e+07

10.04.2002 11:00:00
,000000
2,77766e+07
2,81367e+07
2,80526e+07

10.04.2002 11:10:00
,000000
2,77809e+07
2,8141e+07
2,8057e+07

10.04.2002 11:20:00
,000000
2,77888e+07
2,8149e+07
2,80649e+07

10.04.2002 11:30:00
,000000
2,78072e+07
2,81672e+07
2,80834e+07

10.04.2002 11:40:00
,000000
2,7821e+07
2,81806e+07
2,80972e+07

10.04.2002 11:50:00
,000000
2,78359e+07
2,81952e+07
2,8112e+07

10.04.2002 12:00:00
,000000
2,78491e+07
2,82079e+07
2,81251e+07

10.04.2002 12:10:00
,000000
2,78606e+07
2,8219e+07
2,81365e+07

10.04.2002 12:20:00
,000000
2,78663e+07
2,82242e+07
2,81421e+07

10.04.2002 12:30:00
,000000
2,78743e+07
2,82316e+07
2,815e+07

10.04.2002 12:40:00
,000000
2,78802e+07
2,8237e+07
2,81557e+07

10.04.2002 12:50:00
,000000
2,78868e+07
2,8243e+07
2,81622e+07

10.04.2002 13:00:00
,000000
2,78965e+07
2,82522e+07
2,81718e+07

10.04.2002 13:10:00
,000000
2,79044e+07
2,82594e+07
2,81795e+07

10.04.2002 13:20:00
,000000
2,79106e+07
2,82651e+07
2,81856e+07

10.04.2002 13:30:00
,000000
2,79216e+07
2,82755e+07
2,81964e+07

10.04.2002 13:40:00
,000000
2,79258e+07
2,82791e+07
2,82005e+07

10.04.2002 13:50:00
,000000
2,79336e+07
2,82863e+07
2,82081e+07

10.04.2002 14:00:00
,000000
2,79411e+07
2,82933e+07
2,82155e+07

10.04.2002 14:10:00
,000000
2,79487e+07
2,83003e+07
2,82229e+07

10.04.2002 14:20:00
,000000
2,79576e+07
2,83086e+07
2,82316e+07

10.04.2002 14:30:00
,000000
2,79705e+07
2,83211e+07
2,82445e+07

10.04.2002 14:40:00
,000000
2,79799e+07
2,833e+07
2,82538e+07

10.04.2002 14:50:00
,000000
2,79856e+07
2,8335e+07
2,82592e+07

10.04.2002 15:00:00
,000000
2,79941e+07
2,83428e+07
2,82675e+07

10.04.2002 15:10:00
,000000
2,80002e+07
2,83482e+07
2,82734e+07

10.04.2002 15:20:00
,000000
2,80089e+07
2,83564e+07
2,8282e+07

10.04.2002 15:30:00
,000000
2,80182e+07
2,83652e+07
2,82911e+07

10.04.2002 15:40:00
,000000
2,80271e+07
2,83735e+07
2,82999e+07

10.04.2002 15:50:00
,000000
2,80322e+07
2,83779e+07
2,83047e+07

10.04.2002 16:00:00
,000000
2,80375e+07
2,83825e+07
2,83098e+07

10.04.2002 16:10:00
,000000
2,80433e+07
2,83877e+07
2,83154e+07

10.04.2002 16:20:00
,000000
2,80463e+07
2,839e+07
2,83181e+07

10.04.2002 16:30:00
,000000
2,80549e+07
2,83981e+07
2,83266e+07

10.04.2002 16:40:00
,000000
2,80648e+07
2,84076e+07
2,83363e+07

10.04.2002 16:50:00
,000000
2,80756e+07
2,84179e+07
2,8347e+07

10.04.2002 17:00:00
,000000
2,8089e+07
2,84309e+07
2,83603e+07

10.04.2002 17:10:00
,000000
2,81004e+07
2,84417e+07
2,83715e+07

10.04.2002 17:20:00
,000000
2,81103e+07
2,84512e+07
2,83812e+07

10.04.2002 17:30:00
,000000
2,81176e+07
2,84581e+07
2,83883e+07

10.04.2002 17:40:00
,000000
2,81298e+07
2,84699e+07
2,84004e+07

10.04.2002 17:50:00
,000000
2,81466e+07
2,84866e+07
2,84172e+07

10.04.2002 18:00:00
,000000
2,81631e+07
2,8503e+07
2,84337e+07

10.04.2002 18:10:00
,000000
2,81816e+07
2,85213e+07
2,84522e+07

10.04.2002 18:20:00
,000000
2,82029e+07
2,85426e+07
2,84735e+07

10.04.2002 18:30:00
,000000
2,8224e+07
2,85637e+07
2,84946e+07

10.04.2002 18:40:00
,000000
2,82507e+07
2,85905e+07
2,85215e+07

10.04.2002 18:50:00
,000000
2,82875e+07
2,86276e+07
2,85585e+07

10.04.2002 19:00:00
,000000
2,83261e+07
2,86667e+07
2,85974e+07

10.04.2002 19:10:00
,000000
2,83598e+07
2,87007e+07
2,86313e+07

10.04.2002 19:20:00
,000000
2,83883e+07
2,87295e+07
2,86601e+07

10.04.2002 19:30:00
,000000
2,84169e+07
2,87584e+07
2,86888e+07

10.04.2002 19:40:00
,000000
2,84568e+07
2,87987e+07
2,8729e+07

10.04.2002 19:50:00
,000000
2,85044e+07
2,8847e+07
2,8777e+07

10.04.2002 20:00:00
,000000
2,85673e+07
2,89108e+07
2,88404e+07

10.04.2002 20:10:00
,000000
2,8628e+07
2,89725e+07
2,89016e+07

10.04.2002 20:20:00
,000000
2,86915e+07
2,9037e+07
2,89656e+07

10.04.2002 20:30:00
,000000
2,87584e+07
2,91051e+07
2,9033e+07

10.04.2002 20:40:00
,000000
2,88343e+07
2,91826e+07
2,91096e+07

10.04.2002 20:50:00
,000000
2,89086e+07
2,92583e+07
2,91844e+07

10.04.2002 21:00:00
,000000
2,89821e+07
2,93334e+07
2,92585e+07

10.04.2002 21:10:00
,000000
2,90489e+07
2,94017e+07
2,9326e+07

10.04.2002 21:20:00
,000000
2,91221e+07
2,94766e+07
2,93998e+07

10.04.2002 21:30:00
,000000
2,92027e+07
2,95589e+07
2,9481e+07

10.04.2002 21:40:00
,000000
2,92849e+07
2,96429e+07
2,9564e+07

10.04.2002 21:50:00
,000000
2,93671e+07
2,9727e+07
2,96469e+07

10.04.2002 22:00:00
,000000
2,94493e+07
2,98111e+07
2,97298e+07

10.04.2002 22:10:00
,000000
2,95316e+07
2,98952e+07
2,98128e+07

10.04.2002 22:20:00
,000000
2,96139e+07
2,99794e+07
2,98959e+07

10.04.2002 22:30:00
,000000
2,96961e+07
3,00636e+07
2,99788e+07

10.04.2002 22:40:00
,000000
2,97783e+07
3,01478e+07
3,00617e+07

10.04.2002 22:50:00
,000000
2,98604e+07
3,02319e+07
3,01446e+07

10.04.2002 23:00:00
,000000
2,99426e+07
3,03162e+07
3,02276e+07

10.04.2002 23:10:00
,000000
3,00246e+07
3,04003e+07
3,03105e+07

10.04.2002 23:20:00
,000000
3,01068e+07
3,04846e+07
3,03934e+07

10.04.2002 23:30:00
,000000
3,01889e+07
3,05688e+07
3,04764e+07

10.04.2002 23:40:00
,000000
3,02711e+07
3,0653e+07
3,05594e+07

10.04.2002 23:50:00
,000000
3,03533e+07
3,07372e+07
3,06423e+07

11.04.2002 00:00:00
,000000
3,04355e+07
3,08214e+07
3,07252e+07

11.04.2002 00:10:00
,000000
3,05178e+07
3,09058e+07
3,08083e+07

11.04.2002 00:20:00
,000000
3,06001e+07
3,09901e+07
3,08913e+07

11.04.2002 00:30:00
,000000
3,06824e+07
3,10744e+07
3,09743e+07

11.04.2002 00:40:00
,000000
3,07647e+07
3,11587e+07
3,10573e+07

11.04.2002 00:50:00
,000000
3,08469e+07
3,1243e+07
3,11403e+07

11.04.2002 01:00:00
,000000
3,09291e+07
3,13272e+07
3,12233e+07

11.04.2002 01:10:00
,000000
3,10113e+07
3,14114e+07
3,13063e+07

11.04.2002 01:20:00
,000000
3,10935e+07
3,14956e+07
3,13892e+07

11.04.2002 01:30:00
,000000
3,11756e+07
3,15798e+07
3,14722e+07

11.04.2002 01:40:00
,000000
3,12578e+07
3,16641e+07
3,15551e+07

11.04.2002 01:50:00
,000000
3,13399e+07
3,17482e+07
3,16381e+07

11.04.2002 02:00:00
,000000
3,14221e+07
3,18325e+07
3,17211e+07

11.04.2002 02:10:00
,000000
3,15043e+07
3,19167e+07
3,1804e+07

11.04.2002 02:20:00
,000000
3,15864e+07
3,20008e+07
3,1887e+07

11.04.2002 02:30:00
,000000
3,16686e+07
3,20851e+07
3,197e+07

11.04.2002 02:40:00
,000000
3,17508e+07
3,21693e+07
3,20531e+07

11.04.2002 02:50:00
,000000
3,1833e+07
3,22535e+07
3,21361e+07

11.04.2002 03:00:00
,000000
3,19152e+07
3,23377e+07
3,22191e+07

11.04.2002 03:10:00
,000000
3,19974e+07
3,24219e+07
3,23021e+07

11.04.2002 03:20:00
,000000
3,20795e+07
3,25061e+07
3,23851e+07

11.04.2002 03:30:00
,000000
3,21618e+07
3,25904e+07
3,24682e+07

11.04.2002 03:40:00
,000000
3,22441e+07
3,26747e+07
3,25513e+07

11.04.2002 03:50:00
,000000
3,23263e+07
3,27589e+07
3,26343e+07

11.04.2002 04:00:00
,000000
3,24086e+07
3,28432e+07
3,27174e+07

11.04.2002 04:10:00
,000000
3,24908e+07
3,29275e+07
3,28005e+07

11.04.2002 04:20:00
,000000
3,25731e+07
3,30118e+07
3,28835e+07

11.04.2002 04:30:00
,000000
3,26553e+07
3,3096e+07
3,29666e+07

11.04.2002 04:40:00
,000000
3,27375e+07
3,31803e+07
3,30496e+07

11.04.2002 04:50:00
,000000
3,28198e+07
3,32645e+07
3,31326e+07

11.04.2002 05:00:00
,000000
3,29021e+07
3,33487e+07
3,32158e+07

11.04.2002 05:10:00
,000000
3,29845e+07
3,34330e+07
3,32989e+07

11.04.2002 05:20:00
,000000
3,30666e+07
3,35172e+07
3,33819e+07

11.04.2002 05:30:00
,000000
3,3149e+07
3,36015e+07
3,34651e+07

11.04.2002 05:40:00
,000000
3,32312e+07
3,36857e+07
3,35481e+07

11.04.2002 05:50:00
,000000
3,33133e+07
3,37698e+07
3,36311e+07

11.04.2002 06:00:00
,000000
3,33956e+07
3,3854e+07
3,37141e+07

11.04.2002 06:10:00
,000000
3,34781e+07
3,39382e+07
3,37973e+07

11.04.2002 06:20:00
,000000
3,35604e+07
3,40224e+07
3,38804e+07

11.04.2002 06:30:00
,000000
3,36428e+07
3,41066e+07
3,39635e+07

11.04.2002 06:40:00
,000000
3,37252e+07
3,41908e+07
3,40466e+07

11.04.2002 06:50:00
,000000
3,38075e+07
3,42748e+07
3,41296e+07

11.04.2002 07:00:00
,000000
3,38897e+07
3,4359e+07
3,42127e+07

11.04.2002 07:10:00
,000000
3,39719e+07
3,4443e+07
3,42957e+07

11.04.2002 07:20:00
,000000
3,40541e+07
3,4527e+07
3,43787e+07

11.04.2002 07:30:00
,000000
3,41363e+07
3,4611e+07
3,44617e+07

11.04.2002 07:40:00
,000000
3,42186e+07
3,46951e+07
3,45447e+07

11.04.2002 07:50:00
,000000
3,43009e+07
3,47791e+07
3,46277e+07

11.04.2002 08:00:00
,000000
3,43832e+07
3,48632e+07
3,47108e+07

11.04.2002 08:10:00
,000000
3,44655e+07
3,49473e+07
3,47938e+07

11.04.2002 08:20:00
,000000
3,45477e+07
3,50313e+07
3,48767e+07

11.04.2002 08:30:00
,000000
3,46299e+07
3,51154e+07
3,49596e+07

11.04.2002 08:40:00
,000000
3,47121e+07
3,51994e+07
3,50426e+07

11.04.2002 08:50:00
,000000
3,47944e+07
3,52835e+07
3,51256e+07

11.04.2002 09:00:00
,000000
3,48766e+07
3,53677e+07
3,52086e+07

11.04.2002 09:10:00
,000000
3,4959e+07
3,54519e+07
3,52916e+07

