[image: image1.wmf]Executives:
Gert Torbohm / Arndt Hensky

Date:
10/01/2001

EW1.5 Parameter List


[image: image2.png]ENRON WIND





Designation of screen pages under which the parameters are described

Page
monitor screen page title:
Page
monitor screen page title:
Page
monitor screen page title:








1
Rotational Speeds 1
11
Azimuth
21
Passwords

2
Rotational Speeds 2
12
Blade Angle
22
Enable Errors

3
Rotational Speeds 3
13
Temperatures
23
System Parameters 1

4
Power
14
Temperature Control
24
Status Displays

5
Torque
15
Voltage Control
25
Pitch Status 

6
Wind 1
16
Rot. Speed Control
26
System Parameters 2

7
Wind 2
17
Blade Angle Part load
27
Low-noise Operation 

8
Timeout Periods
18
Mains Parameters 1
28
Reserved

9
Hydraulics
19
Production Data
29
CAN / CCU Diagnosis

10
Gearbox / Heating
20
Mains Parameters 2
30
Scope function

.

Screen /

Parameter

Number
Parameter Designation

Rotational Speeds 1
Functional Description
Rel.

FM

1.1
generator overspeed
maximum generator speed before the error GENERATOR OVERSPEED appears
14

1.2
generator overspeed period
delay period for the GENERATOR OVERSPEED error
14

1.3
rotor overspeed
maximum rotor speed before the error ROTOR OVERSPEED appears
15

1.4
rotor overspeed period
delay period for the ROTOR OVERSPEED error
15

1.5
ratio generator/rotor
ratio generator / rotor speed, gearbox ratio
-

1.6
Max. permissible deviation gen./rot.
maximum allowable deviation in the ratio of generator / rotor
57

129

1.7
Gen./rot. deviation time
time for the maximum deviation in the ratio of gen./rotor
57

129

1.8
Min. speed, tower resonance
lower limit of the tower resonance range for generator speed
110

1.9
Max. speed, tower resonance
upper limit of the tower resonance range for generator speed
110

1.10
Time, speed, tower resonance
max. time for generator speed in the tower resonance range
110

1.11
min. gen. speed sensor monitoring
lowest gen. speed for monitoring: rotational speed sensor, deviation gen./rotor


1.12
reserved



Screen /

Parameter

Number
Parameter Designation

Rotational Speeds 2
Functional Description

2.1
start spinning speed
temporally averaged spinning generator speed with fixed blade angle (P12.2) at which the turbine starts up to load operation.

2.2
storm spinning speed
spinning generator speed with fixed blade angle (P12.2) at which the turbine cannot start up to load operation if exceeded (too much wind)

2.3
spinning averaging period
the time in which the spinning speed is averaged

2.4
minimum spinning time
the minimum time in which the turbine remains in spinning mode

2.5
start speed fast ramp
generator speed at which a large ramp gradient (P2.7) is accelerated when starting up

2.6
start speed slow ramp
generator speed at which a low ramp gradient (P2.8) is continued when starting up

2.7
fast ramp gradient
ramp gradient, with which acceleration is between P2.5 and P2.6  when starting up 

2.8
slow ramp gradient
ramp gradient, with which acceleration is under P2.5 and over P2.6  when starting up

2.9
Max. speed deviation
max. generator speed deviation (setpoint - current value), at which start up is interrupted (without an error message)

2.10
min. gen. speed for rotor braking
Generator speed, below which the rotor disk brake is applied with normal operating braking

2.11
min. gen. speed for hard braking
Generator speed, above which the hard disk brake is applied during a fast braking procedure (6a)

2.12
Factor minimum idling time
Starting up delayed after 3 short gride connections (t_connect < 15 min) (Saving life time of synch. switch)

Screen /

Parameter

Number
Parameter Designation

Rotational Speeds 3
Functional Description

3.1
Setpoint speed, partial load 1
Generator speed setpoint in lower part load operation

3.2
Setpoint speed, partial load 2
Generator speed setpoint in upper part load operation

3.3
Setpoint speed, full load
Generator speed setpoint in full-load operation

3.4
min. load generator speed
minimum generator speed in load operation (cut-out speed)

3.5
max. load generator speed
maximum generator speed in load operation

3.6
gen.speed switchover part load
switching generator speed from lower partial load range into higher speed range, it must lie between P3.1 and P3.2 (67m tower) and P1.8 (80/85m tower) 

3.7
gen.speed switchover upper part load
switching generator speed into upper partial load range, it must lie between P1.9 and P3.2,

only valid for 80/85m tower, for which the resonance frequency lies in the load operation speed range (P1.8 > P3.4)

3.8
Cut-in speed
Generator speed at which the frequency converter can be switched in

3.9
rotor pulses per rev.
number of pulses from ind. proximity switch per rotor revolution 

3.10
generator pulses per rev.
number of pulses from ind. proximity switch per generator revolution

3.11
rotor speed scaling
specification of the speed at which the frequency analog converter voltage = 10V

(no longer required)

3.12
generator speed scaling
Generator speed scale corresponds to 20mA as an analog signal coming from the frequency converter



Screen /

Parameter

Number
Parameter Designation

Power
Functional Description
Rel.

FM

4.1
rated power
generator rated power
-

4.2
Gen. peak power
max. allowable generator power
23

4.3
Time gen. peak power
period of max. allowable generator power
23

4.4
Max. power demand
max. power demand, reached at latest above rated wind and not exceeded
-

4.5
delay lock line cut-in
delay time in wind park in switching in to the grid, to avoid two turbines going onto the grid simultaneously, should be set differently for each turbine in wind park 
-

4.6
reserved



4.7
minimum power
Cut-out condition for power with falling wind speed
-

4.8
minimum power period
Cut-out power averaging time
-

4.9
gen. cut-out power
undershooting power during braking procedure instantaneously disconnects generator from grid 
-

4.10
max. motor power
highest allowable motor power before the error MAX. MOTORIC triggered
19

4.11
power signal offset
power display set to zero at  0 kW
-

4.12
Cos Phi, set point
Setpoint for cos phi to the frequency converter, only valid for deactivated voltage control (P15.1=0), for gen. power < P4.15,

valid range : -0.9..-1 inductive, 0.9..1 : capacitive
-

4.13
Cos Phi, power-dependent
Setpoint for power factor (cos phi) at high power, for gen. power > P4.14, 

valid range : -0.9..-1 inductive, 0.9..1 : capacitive
-

4.14
Power factor control ON
Power for reactive power control = ON with power factor=P4.13
-

4.15
Power factor control OFF
Power for reactive power control = OFF with power factor=P4.13
-

Screen /

Parameter

Number
Parameter Designation

Torque
Functional Description

5.1
rated torque
rated generator torque, reference parameter for the torque displays to visualize and assign to frequency converter

5.2
max. torque gradient
max. change of torque during controlling

5.3
Max. torque demand
upper limit for speed controller output torque demand 

5.4
Min. torque demand
lower limit for speed controller output torque demand

5.5
torque switch. -> upper part load
switching torque from lower to upper part load range, only valid for soft tower, for which the resonance frequency is in power operation speed range (P1.8 > P3.4). The value is calculated automaticaly by the PLC, no manual setting is necessary!

5.6
torque switch-> low. part. load
switching torque from upper to lower part load range, only valid for soft tower, for which the resonance stimulation frequency is in power operation speed range (P1.8 > P3.4) ). The value is calculated automaticaly by the PLC, no manual setting is necessary!

5.7
torque switching period
averaging time for switching between lower and upper part load, only valid for 80m tower

5.8
corr. fact. torque char. curve
correction factor for the aerodynamic characteristic curve  

Tdemand = f * k / T * N² in variable speed range. (f = P5.8, T : abs. temp.)

To be set individually depending on blade characteristics, site height...

5.9
max. torque N>TR.-> N<TR.
maximum torque demand scanning through tower resonance range

5.10
torque scaling
maximum torque demand and current value to/from converter, corresponds to 20mA as an analog signal

5.11
power curve deact.
deactivation of calculation of the power curve, if P5.11 > 0, to be set

e.g. while power limit tests

5.12
corr. fact. power/torque
correction factor to adapt the max. power demand P4.4. 

Screen /

Parameter

Number
Parameter Designation

Wind 1
Functional Description
Rel. 

FM

6.1
Yaw start wind
minimum wind speed, at which automatic wind direction tracking takes place
-

6.2
Start wind averaging time
averaging period for the lower wind speed limit, at which an automatic  wind direction tracking is initiated
-

6.3
restart wind after storm
wind speed for restart after storm shutdown
-

6.4
restart after storm period
averaging period for restart after storm shutdown
-

6.5
storm shutdown
if the wind speed average (t=P6.6) is greater than the parameter value, a storm shutdown follows
7

6.6
storm shutdown period
averaging period, over which the wind speed is averaged for storm shutdown
7

6.7
storm gusts
if the wind speed average (t=P6.8) is greater than the parameter value, a storm shutdown follows
7

6.8
storm gusts period
averaging period for storm gust shutdown
7

6.9
anemometer monit. P<wind
parameter to monitor the anemometer. If the generator power > P6.9 and wind speed < 4 m/s, the ANEMOMETER ERROR is triggered
54

6.10
anemometer monitoring delay
averaging period, over which the power and wind speed is averaged for triggering the ANEMOMETER fault message
54

6.11
Reserved



6.12
Manual On Heater Windmeas.
With P6.12 = 1 the heaters for the wind measurement devices is switched on permanently 
-

Screen /

Parameter

Number
Parameter Designation

Wind 2
Functional Description
Rel.

FM

7.1
anemometer offset
anemometer calibration option, this parameter is added to internal measured variable
-

7.2
anemometer multiplier
Anemometer calibration option. The internal measured variable is multiplied with this parameter
-

7.3
anemometer divisor
Anemometer calibration option. The internal measured variable is divided by this parameter
-

7.4
Switchover wind, acceleration alarm 2
Double parameter wind speed for drive train monitoring

From V1x023: e.g. P7.4= 10,5 m/s

Lower alarm level drive train monitor valid up to 10m/s

Upper alarm level drive train monitor valid from (10 + 5 =) 15 m/s

Between: alarm level is a linear function of the 10sec average of wind speed
176

7.5
max. wind deviation 1 sec
Max. deviation between wind direction and nacelle position 

(1 sec averaged)
180

7.6
max. wind deviation 10 sec
Max. deviation between wind direction and nacelle position 

(10 sec averaged)
180

7.7
tower acc. alarm 1
max. tower acceleration threshold value
177

7.8
tower acc. alarm delay 1
tower acceleration monitoring delay time
177

7.9
tower acc. Alarm 2
Double parameter threshold for max. drive train oscilation

from V1x023: e.g. P7.9 = 604

lower alarm level drive train monitor = 600

upper alarm level drive train monitor = 600+400 = 1000

(see P7.4)
176

7.10
tower acc. alarm delay 2
Drive train acceleration monitoring delay time
176

7.11
tower acc. test level
threshold value for activation of tower resonance frequency measurement and monitoring vibration sensor during fault shutdown
41

7.12
vibration control
vibration control monitoring PCH 

bit0: analog channel 1  available

bit1: dig. alarm channel 1 available 

bit2: analog channel 2 available

bit3: dig. alarm channel 2 available 

Bit4: error signal deactivated

Bit5: test signal deactivated

Bit6: activating man. Test (attention : leads to swiching-off the WEC)

bit15: Activating drive train monitor by speed variance (bit2=0! -> PCH not used for drive train monitor)
41

176

177

Screen /

Parameter

Number
Parameter Designation

Timeout Times
Functional Description
Rel.

FM

8.1
starting delay
release for automatic restart only given after this period
87

8.2
cut-in delay time
time delay, for which the blade angle must be greater than 4° (or 2° for P3.8 > 1200 rpm), before the generator is switched in
-

8.3
Max. idle time
maximum time in idling for cut-in, shutdown in spinning operation follows if exceeded
-

8.4
generator filter period
delay period for generator filter soiling warning
109

8.5
pitch brake period
max. rotor blade turning period to feathered pitch pos. for battery shutdown (brake procedures 5-6)
130

131

132

8.6
secondary braking period
max. braking time for brake procedures 6-7 with application of the disk brake
27

8.7
Max. shutdown time
max. braking period for brake procedure 2 with blade adjustment
24

8.8
Battery charging time
waiting period to recharge batteries after battery voltage fault (212-214) or braking time fault after battery shutdown (130-132)
133

8.9
min. pitch diff. in 3s while batt.switching-off
Min. angle range, which the blades should turn while battery switching-off from second to fifth second
130

131

132

8.10
Time betw. soft and hard braking
Time period between the triggering of valves for soft and hard braking while engaging disk brake after manual stop or remote stop (only if bit 7 is set of P26.3
-

8.11
brush wear delay
Delay period between generator brush wear signal and turbine shut down
153

8.12
reserved



Screen /

Parameter

Number
Parameter Designation

Hydraulics
Functional Description
Rel.

FM

9.1
brake cooling period
Cooling time for the brakes, when braked through an error or manually. A restart is only allowable after this period.
-

9.2
filter period delay
reaction period, after which the turbine is braked after detection of HYDRAULIC FILTER SOILING error, not used
-

9.3
hydraulic oil level period
reaction time to loss of hydraulic oil level indicator input signal, not used  
-

9.4
min. pumping time interval
assigned minimum allowed interval time between two pumping activities of hydraulic motor 
46

9.5
max. pumping time
assigned maximum allowed pumping time for hydraulic motor
45

9.6
Suppression, brake not free 
period in which the error BRAKE NOT RELEASED is evaluated after the brake is released
34

9.7
delay in release
period after which the brake valve is driven following de-airing valve after releasing the brake (not used)
-

9.8
hydraulic 1 / 2 contact
1: system pressure control with inbuilt hysteresis ( EDS 500 )

2: system pressure control with 2 pressure switches (not used)
-

9.9
brake not released period
if, after the secondary brake activation, the correct “brake released” acknowledgement does not appear within the parameterized period, the error BRAKE NOT RELEASED appears
34

9.10
reserved



9.11
reserved



9.12
reserved



Screen /

Parameter

Number
Parameter Designation

Gearbox / Heating
Functional Description


10.1
gearbox oil pressure period
reaction time to the loss of the gearbox oil pressure input signal
52

10.2
gearbox oil level period
reaction time to the loss of the gearbox oil level input signal
51

10.3
Release heater  (0/1)
0: blocks gearbox oil heating

1: release for gearbox oil heating
-

10.4
Activation temp., gearbox oil heat.
gearbox oil heating cut-in temperature Tgearb. < Theat on
-

10.5
Deactivation temp., gearbox oil heat.
gearbox oil heating cut-out temperature Tgearb. > Theat off
-

10.6
gearbox filter period
delay period disturbance gearbox filter soiling
71

89

10.7
nacelle heating cut-in delay
cut-in delay in nacelle heating (not used)
--

10.8
oil monitoring cut-in delay
cut-in delay for the monitoring of gearbox oil pressure after activating of oil pump
52

10.9
oil cooler cut-in temp.
oil cooler cut-in temperature Tgearb. > Tcooler on
-

10.10
oil cooler cut-out temp.
oil cooler cut-out temperature Tgearb. < Tcooler off
-

10.11
reserved



10.12
reserved



Screen /

Parameter

Number
Parameter Designation

Azimuth
Functional Description
Rel. FM



11.1
Timer yaw right, left
period, after which, the wind direction tracking is activated after a constant orientation signal from the wind vane
-

11.2
Counter yaw right, left
period, after which, the wind direction tracking is activated after an avaraging orientation signal from the wind vane
-

11.3
base tracking period
period, in which wind direction tracking is continued after identification of the first change in center signal from the wind vane 
-

11.4
azimuth direction
nacelle head cable orientation 
-

11.5
nacelle revs. to stop
cable unwind release for idling / spinning mode and exceeding the number of nacelle revolutions
20

21

11.6
nacelle revs. to unwinding
number of nacelle revolutions, for which the cable unwinding is started, independent of the wind speed, except extrem storm
20

21

11.7
nacelle revs. to end position
maximum number of nacelle revolutions before the AZIMUTH END error is triggered
22

11.8


tooth counter off-period
off-period after counting up a tooth of the head to avoid multiple counting
-

11.9
tooth to tooth timeout
if the parameter period passes with no pulse counted from the two azimuth head sensors with the azimuth motor driven, the error TIMEOUT AZIMUTH COUNTER is triggered
31

11.10.
teeth per head
number of teeth on the azimuth bearing gear tooth head 
-

11.11
Offset to north
cable orientation angular offset to the northern direction
-

11.12
reserved



Screen /

Parameter

Number
Parameter Designation

Blade Angle
Functional Description
Rel.

FM

12.1
feathered pitch position
blade angle in feathered pitch position (stationary)
-

12.2
Spinning blade angle
blade angle spinning (free running)
-

12.3
max. control pitch rate
maximum blade angle speed in controlling operation
-

12.4
pitch rate during disturbance
blade angle speed during disturbance
-

12.5
Pitch rate during manual operation
blade angle speed in manual pitch operation
-

12.6
Min. blade angle demand
minimum demand blade angle during start-up. Should be set on a value closed to P17.5. P12.6<<P17.5 can cause going on/off-grid too often when there is weak wind.
-

12.7
Max. blade angle deviation
max blade angle deviation (demand – current), a 6x value is allowable during braking
145

12.8
Max. time for blade angle deviation
max. blade angle deviation period
145

12.9
max. blade asymmetry
max. blade asymmetry, monitoring the deviation of the blade angle values among themselves
144

12.10
max. blade asymmetry period
max. blade asymmetry period
144

12.11
max. blade angle in load op.
max. blade angle in load operation, if exceeded with the delay P6.8 a storm shutdown is triggered
7

12.12
axle disturbance period
delay period, after which the ‘axle disturbance’ fault message is triggered
121

149

150

12.13
PLC port communication pitch (3,4)
Setting COM3 or COM4 as communication port of the PLC (Slave) to the pitch controller. Changing of setting is valid only after a reboot of the PLC
-

Screen /

Parameter

Number
Parameter Designation

Temperatures
Functional Description
Rel.

FM



13.1
Winding 1 overtemperature
maximum allowable generator windings temperature 1, automatic restart below P13.1 - 15°C
99

13.2
Winding 2 overtemperature
maximum allowable generator windings temperature 2, automatic restart below P13.2 - 15°C
100

13.3
Reserve



13.4
Generator bearing A overtemperature
maximum allowable temperature of generator bearing A, automatic restart below P13.4 - 15°C
75

13.5
Generator bearing B overtemperature
maximum allowable temperature of generator bearing B, automatic restart below P13.5 - 15°C
76

13.6
Generator cooling air overtemperature
maximum allowable generator air cooling temperature, automatic restart below P13.6 - 15°C
97

13.7
Gearbox oil min. temperature
if the gearbox temperature falls below P13.7, the turbine is stopped, automatic restart above P13.7 + 5°C
84

13.8
Gearbox oil overtemperature
maximum allowable gearbox oil temperature, automatic restart below P13.8 - 15°C
77

13.9
Gearbox bearing A overtemperature
maximum allowable gearbox bearing temperature A, automatic restart below P13.9 - 15°C
98

13.10
Outside min. temperature
minimum allowable outside temperature, automatic restart above P13.10 + 5°C 
78

13.11
Restart temperature
describes how often an automatic restart is allowed after shutdown due to high temperature
88

13.12
Shaft bearing overtemperature
maximum allowable shaft bearing temperature, automatic restart below P13.12 - 15°C
81

13.13
Gearbox bearing B overtemperature
maximum allowable gearbox bearing temperature B, automatic restart below P13.13 - 15°C
76

13.14
container low temp.
Minimum allowable container temperature, automatic restart above  P13.14 + 5°C (only offshore)
190

13.15
container high temp.
maximum allowable container temperature, automatic restart below P13.15 -15°C (only offshore)
190

13.16
converter cooling system temp.
maximum allowable converter cooling system temperature, automatic restart below P13.16 -15°C (only offshore)
197

13.17
Overtemp. transformer warning
Temperature of medium voltage transformer (windings) triggering a warning, automatic reset below P13.17 -15°C (only active if P26.3 Bit5=1)
174

13.18
Overtemp. transformer
Maximum allowable temperature of medium voltage transformer (windings), automatic restart below P13.18 -15°C (only active if P26.3 Bit5=1)
175

Screen /

Parameter

Number
Parameter Designation

Temperature Control
Functional Description

14.1
gen. cooling on temp.
cooling air target temperature or switch-on temperature for generator fan

14.2
fan temp. control amplif.
temperature control amplification on activation (not used)

14.3
T-int. temp. controller, fan
temperature control integration time constant on activation (not used)

14.4
gen. winding on temp.
generator fan cut-in temperature

14.5
Temperature control activation
0: temp. control deactivation

14.6
gen. cooling off temp. 
Cut-out cooling air temperature for generator fan 

14.7
gen. windings off temp.
Cut-out windings temperature for generator fan 

14.8
gen. vert. fan on temp.
generator windings temperature, at which the vertical fan cuts-in

14.9
gen. vert. fan off temp.
generator windings temperature, at which the vertical fan cuts-out

14.10
vert. fan on power
power, with which the vertical fan cuts-in, after exceeding

14.11
vert. fan off power
power, with which the vertical fan is cuts-out, after deceeding 

14.12
reserved


14.13
Min. operation temp. gearbox bypass filtration
Minimum temp. for gearbox bypass filtrat.pump, switching-on at oil temp. > P14.13, switching-off at oil temp. < P14.13 - 5°C (only active if P26.3 Bit2=1)

14.14
Max. operation temp. gearbox bypass filtration
maximum temp. for gearbox auxil. filtrat.pump, switching-on at oil temp. < P14.14, switching-off at oil temp. < P14.14 - 5°C (only active if P26.3 Bit2=1)

14.15
switching on temp. heating CCU cool.system
switching-on temp. heating converter cooling system (only offshore)

14.16
Diff. Switching off temp.heating CCU cool.system
diff. switching-off temp. heating converter cooling system during heating after restart (only offshore)

14.17
switching on temp. fan 1
switching-on temp.fan 1 converter cooling system (only offshore)

14.18
switching on temp. fan 2
switching-on temp.fan 2 converter cooling system (only offshore)

14.19
switching on temp. pump 2/ valves 1,2
switching-on temp. pump 2 / valve 1,2 converter cooling system (only offshore)

Screen /

Parameter

Number
Parameter Designation

Voltage Control
Functional Description

15.1
phi control activation
1 : activation of voltage control with assigned cos-phi as regulated variable

15.2
power control activation
1 : activation of voltage control with power limit as regulated variable

15.3
phi voltage target value
voltage target value with regulation of assigned cos-phi as regulated variable

15.4
power voltage target value
voltage target value for regulation with power limit as regulated variable

15.5
min. power angle
minimum power angle for voltage regulation with power limit with cos-phi as regulated variable

15.6
max. power angle
maximum power angle for voltage regulation with power limit with cos-phi as regulated variable

15.7
phi controller amplif.
voltage controller amplification with assigned cos-phi as regulated variable

15.8
phi int. time controller
voltage controller integration time with assigned cos-phi as regulated variable

15.9
power controller adjust.
controller amplification with power limit as regulated variable

15.10
power int. time controller
controller integration time with power limit as regulated variable

15.11
reserved


15.12
reserved


Screen /

Parameter

Number
Parameter Designation

Rotational Speed Control
Functional Description

16.1
Amplif. controller no-load operation
speed controller amplification during run-up, blade angle as output

16.2
T-int. controller no-load operation
speed controller integration time during run-up

16.3
Amplif. controller full load
speed controller amplification in full-load operation, blade angle as output

16.4
T-int. controller full load
speed controller integration time in full-load operation

16.5
Amplif. controller, low partial load
speed controller amplification in lower partial-load range, torque as output

16.6
T-int. controller, low partial load
speed controller integration time in lower partial-load range, torque as output

16.7
Amplif. controller, upper partial load
speed controller integration time in upper partial-load range, torque as output

16.8
T-int. controller, upper partial load
speed controller integration time in upper partial-load range, torque as output

16.9
Amplif. damping, drive train vibration
drive train vibration damping amplification, if parameter = 0 damper is deactivated

16.10
Damped frequency, drive train
drive train damping frequency 

16.11
rel. degree of damping 
relative degree of drive train damping

16.12
damping delay
damping delay of drive train damping

16.13
PID pitch P-amplif. 
HTurm>=100 m Or EW1.5sl

16.14
PID pitch T-integ.
HTurm>=100 m Or EW1.5sl

16.15
PID pitch T-diff. PI
HTurm>=100 m Or EW1.5sl

16.16
PID pitch P2-amplif.. *1e6
HTurm>=100 m Or EW1.5sl

16.17
PID pitch T2-int. 
HTurm>=100 m or EW1.5sl

16.18
dn/dt limit for adap.2
HTurm>=100 m or EW1.5sl

16.19
reserved


16.20
Max. pitch rate Crossterm during run up
HTurm>=100 m or EW1.5sl

Screen /

Parameter

Number
Parameter Designation

Blade Angle Partial-Load
Functional Description

17.1
power P1
power limit transition blade angle  P17.5 / P17.6

17.2
power P2
power limit transition blade angle  P17.6 / P17.7

17.3
power P3
power limit transition blade angle  P17.7 / P17.8

17.4
power P4
power limit transition blade angle  P17.8 / P17.9

17.5
blade angle P<P1
blade angle at power < P17.1

17.6
blade angle P>P1
blade angle at power > P17.1

17.7
blade angle P>P2
blade angle at power > P17.2

17.8
blade angle P>P3
blade angle at power > P17.3

17.9
blade angle P>P4
blade angle at power > P17.4

17.10
blade offset ang. at rated power
for “peak shavers” turbines having a 100m hub height :

in the partial-load range P > P17.4, the minimum blade angle is set, indep. of power,  according to a linear characteristic curve f(max (Pact , P_10sec-average value)), such that at P=P17.4,  angle = P17.9 and at P=P4.1 
(rated power), angle = P17.9 + P17.10

17.11
reserved


17.12
Averaging time, blade adj. partial load 
minimum period in s, in which the blade angle remains constant in partial-load 

17.13
Devisor pitch amplification devisor at Teta_B
HTurm>=100 m or EW1.5sl 

17.14
teta_A offset pitch adap.1
HTurm>=100 m or EW1.5sl

17.15
teta_B offset pitch adap.2
HTurm>=100 m or EW1.5sl

Screen /

Parameter

Number
Parameter Designation

Mains Variables 1
Functional Description

18.1
line frequency
line base frequency (not used)

18.2
ratio U-converter
voltage converter ratio (not used)

18.3
ratio I-converter
current converter ratio (not used)

18.4
KU-monitoring limit value
KU-monitoring limit value (not used)

18.5
Max. voltage deviation between phases
maximum voltage deviation between the 3 phases

18.6
reserved


18.7
reserved


18.8
net. data analog (0) serial (1)
switching, how the mains data are measured : (not used)
0 : analog from Multi-MU via PS416-AIN,

1 : serial from mains monitor NÜ1 via SucoNet.

18.9
offset voltage
voltage offset for signal measurement

18.10
reserved


18.11
reserved


18.12
meas. system man. trigger
Activates dig. and analog output signals to measuring system (optional)

Screen /

Parameter

Number
Parameter Designation

Production Data
Functional Description

19.1
production
set value for production 

19.2
reserve


19.3
consumption
set value for consumption

19.4
reserve


19.5
operating period
set value for operating hours (turbine on line)

19.6
turbine ok
set value for turbine OK period (ready for operating)

19.7
downtime
set value for downtime

19.8
turbine ok, until last month
set value for turbine OK period until last month

19.9
downtime until last month
set value for downtime until last month

19.10
maintenance period
set value for maintenance period

19.11
repair period
set value for repair period

19.12
maintenance period until last month
set value for maintenance period until last month

19.13
repair period until last month
set value for repair period until last month

19.14
operating period until last month
set value for operating period until last month

Screen /

Parameter

Number
Parameter Designation

Mains Data


Functional Description
Rel.

FM

20.1
overvoltage
max. line voltage
8

20.2
undervoltage
min. line voltage
9

20.3
overfrequency
not used
-

20.4
underfrequency
not used
-

20.5
current asymmetry
Asymmetry monitoring of phase currents
13

20.6
phase angle
not used
-

20.7
overvoltage reaction
overvoltage reaction
8

20.8
undervoltage reaction
undervoltage reaction
9

20.9
overfrequency reaction
not used
-

20.10
undefrequency reaction
not used
-

20.11
multi meas. transd. scaling volt. 
Max. voltage value of the effective power measuring sensor
-

20.12
multi meas. transd. scaling curr.
Max. current value of the effective power measuring sensor 
-

20.13
TimeDelay Ground fault control
Ground fault LowVoltageMainDistribution
207

Screen /

Parameter

Number
Parameter Designation

Passwords


Functional Description

21.1



21.2



21.3



21.4



21.5



21.6



21.7



21.8
reserved


21.9
reserved


21.10
reserved


21.11
reserved


21.12
reserved


Screen /

Parameter

Number
Parameter Designation

Enable Errors


Functional Description

22.1
enable errors 16 -1
activation and deactivation of errors. 0 = active / 1 not active

22.2
enable errors 32 - 17
activation and deactivation of errors. 0 = active / 1 not active

22.3
enable errors 48 - 33
activation and deactivation of errors. 0 = active / 1 not active

22.4
enable errors 64- 49
activation and deactivation of errors. 0 = active / 1 not active

22.5
enable errors 80 - 65
activation and deactivation of errors. 0 = active / 1 not active

22.6
enable errors 96 - 81
activation and deactivation of errors. 0 = active / 1 not active

22.7
enable errors 112 - 97
activation and deactivation of errors. 0 = active / 1 not active

22.8
enable errors 128 - 113
activation and deactivation of errors. 0 = active / 1 not active

22.9
enable errors 144 - 129
activation and deactivation of errors. 0 = active / 1 not active

22.10
enable errors 160 - 145
activation and deactivation of errors. 0 = active / 1 not active

22.11
enable errors 176 - 161
activation and deactivation of errors. 0 = active / 1 not active

22.12
enable errors 192 - 177
activation and deactivation of errors. 0 = active / 1 not active

22.13
enable errors 208- 193
activation and deactivation of errors. 0 = active / 1 not active

22.14
enable errors 224- 209
activation and deactivation of errors. 0 = active / 1 not active

Screen /

Parameter

Number
Parameter Designation

System Parameters


Functional Description

23.1
WGT type
entry of the WGT type: 
1522 : series-EW1.5 /s 

1523 : EW1.5sl

1543 : EW1.5o

1552 : series-EW1.5 /s with CAN

1553 : EW1.5sl with CAN

23.2
ID number 1
the low word of the ID number is requested while establishing the connection between the PC on site and remote monitoring, to control the remote monitoring access options (not used for VisuPro)

23.3
ID number 2
the high word of the ID number is requested while establishing the connection between the PC on site and remote monitoring, to control the remote monitoring access options (not used for VisuPro)

23.4
WGT number
last four digits of the commission number

5 digits of commissions number (one 0 less after 15...)

23.5
number of computer restarts
number, as the PC booted on account of PLC – PC communication errors

23.6
modem test (0/1)
activation of a control call

23.7
deactiv. reset end position 
0 : activation, 1 : deactivation, automatically drive pitch from its end position with STOP/RESET

23.8
software variant
0 : EW1.5s, Bit 2 = 1 for EW1.5sl or/and 100m towers

23.9
reserved


23.10
reserved


23.11
reserved


23.12
reserved


Screen /

Parameter

Number
Parameter Designation

Status Display


Functional Description
Rel.

FM

24.1
version number
PLC program version
-

24.2
secondary braking test
time in hours until the next brake test
38

24.3
announce sec. braking test
a 1 shows, that the brake test time interval has expired and should be carried out when a power of 500 kW occurs
38

24.4
battery test
time in hours until the next battery test
135

24.5
announce battery test
a 1 shows, that the battery test time interval has expired and should be carried out when there is a wind under 3.5 m/s
135

24.6
pitch test
time in hours until the next blade angle test
-

24.7




24.8
status contol system master


diagnosis of PLC at main switch cabinet, each module is represented with one digit, 1=o.k., 2=fault 24V-supply., 9=module faulty, 0=slot standard free,

 modules beginning with FastBus-master from left
62

201

202

24.9
status contol system slave


diagnosis of PLC at  top switch cabinet, each module is represented with one digit, 1=o.k., 2=fault 24V-supply., 9=module faulty, 0=slot standard free,

 modules beginning with FastBus-slave from left
62

201

202

24.10




24.11




24.12




Screen /

Parameter

Number
Parameter Designation

Pitch Status


Functional Description

25.1
dig. inputs axle 1 

bit 0 : fan motor protection, bit 1 : PTC resistor trigger device 130°C, 

bit 2 : PTC resistor trigger device 150°C, bit 3 : end switch 90°,

bit 4 . end switch 0°, bit 5 : battery monitoring, bit 7: pitch service switch 

25.2
dig. inputs axle 2
as P25.1, except bit 7 : battery charge switch relay

25.3
dig. inputs axle 3
as P25.1, except bit 7 : no significance

25.4
axle 1 status
bit 0 : manual drive, bit 1 : drive to parking position, 

bit 2 : reference search run, bit 3 : reference reached, bit 4 : current  = demand, bit 5 : current pos. < min. position, bit 6 : current pos. > max. position, bit 7 : error

25.5
axle 2 status
as P25.4

25.6
axle 3 status
as P25.4

25.7
unit status
bit 0 : reset, bit 1 : stop, bit 2 : start, bit 3 : param. error, Program invalid, bit 4 : end of set, bit 5 : end of block, bit 6 : end of program, bit 7 : error

25.8
reserved


25.9
dig. inputs axle 1 pitch fault
‘frozen’ inputs since last pitch fault, def. see P25.1

25.10
dig. inputs axle 2 pitch fault
‘frozen’ inputs since last pitch fault, def. see P25.2

25.11
dig. inputs axle 3 pitch fault
‘frozen’ inputs since last pitch fault, def. see P25.3

25.12
reserved


Screen /

Parameter

Number
Parameter Designation

System Parameters 2


Functional Description
Rel.

FM

26.1
number of synch. switch on
number of times the synchronous switch has been activated (line connections)


26.2
power switch type 


0 : NZM 12 (Moeller)

1:  M16N1 (Merlin Gerin) or IZM 32 (Moeller) or 3RV (Siemens)


26.3
Selection of components
Bit0=1 : for TZ1.5cal –  turbine to activate the cooling water pump, monitoring cooling water pressure, modified fan control

from V1x024:
Bit1=1: disk brake with 2 valves for hard braking

Bit2=1: activate gearbox bypass filtration

From V1xx25:
Bit3=1: activate watercooling freq. Converter

Bit4=1: NRG anemometer / wind vane

From V1x025 (without CAN), V1x427 (with CAN):

Bit5=1: activate temperature control for medium voltage trans-former with PT100

From V1x026:
Bit6=1: obstruction light

Bit7=1: modified brake procedure


26.4
I/O config. activation CAN-Bus
Bit 0 = 1: Alstom freq. Converter with CAN

Bit 1 = 1: SEG freq. Converter with CAN

Bit 8 = 1: MFR13 with CAN
208

209

26.5
rot. speed/pitch monitor. delay
50ms - average speed rises with falling blade angle -> FM170 delays for a time P26.5 in ms
170

26.6
Max. pitch timeout count
Max. number of pitch controller timeouts
119

26.7
reserved



26.8
reserved



26.9
reserved



26.10
braking type on grid loss
P26.10 = 0 : braking proc. 6a  (immediate application of rotor brake), 

P26.10 = 1 : braking proc. 5  (brake first applied in the feathered pitch position)


26.11
shutdown with brakes 


0 : brake application if n < P2.10 for braking procedures. 2-5, assuming no spinning is permitted in feathered pitch position

1 : immed. brake application in case of battery shutdown (braking procedures 5-6)

2 : immed. brake application in case of fault shutdown (braking procedures 3-6)
-

26.12
Release parameter
Release for changing other important parameters (remains for 10 minutes)
-

Screen /

Parameter

Number
Parameter Designation

Low-Noise Operation


Functional Description
Rel.

FM

27.1
set point rotor speed low-noise op.
rotor speed setpoint for low-noise operation, replaces P3.3 for normal operation. If P27.1 = 0 low-noise operation is deactivated (in 0.1 rpm)
173

27.2
max. power in low-noise op.
maximum power setpoint for low-noise operation, replaces P4.4 for normal operation if P4.4 > P27.2.

If P27.2 = 0 and P27.1 in the allowable range, the max. power is calculated based on a linear characteristic curve depending on P27.1
.-

27.3
blade angle offset in low-noise op.
blade angle offset for low-noise operation in upper partial load operation, P17.8 and 17.9 are added. (in 0.1 °)
-

27.4
direction 1 min.
lower limit of 1st angular range of low-noise wind direction (nacelle previously oriented to the northern direction with P11.11)
-

27.5
direction 1 max.
upper limit of 1st angular range of low-noise wind direction (nacelle previously oriented to the northern direction with P11.11)
-

27.6
direction 2 min.
lower limit of 2nd angular range of low-noise wind direction (nacelle previously oriented to the northern direction with P11.11)
-

27.7
direction 2 max.
upper limit of 2nd angular range of low-noise wind direction (nacelle previously oriented to the northern direction with P11.11)
-

27.8
directional hysteresis
hysteresis angle to switch low-noise operation on and off at the angular range limits
-

27.9
P max wind direction
power level of 10s-avarage for wind direction dependent switching-off of the WEC (P27.1 = 0 and P27.4 < P27.5)
215

27.10
v max wind direction

wind speed level of 4min-avarage for wind direction dependent switching-off of the WEC (P27.1 = 0 and P27.4 < P27.5)
215

27.11
v reset wind direction
wind speed level of 4min-avarage for end of wind direction dependent switching-off of the WEC (undershooting)
-

27.12
reserved



Screen /

Parameter

Number
Parameter Designation

Reserved


Functional Description

28.1
reserved


28.2
reserved


28.3
reserved


28.4
reserved


28.5
reserved


28.6
reserved


28.7
reserved


28.8
reserved


28.9
reserved


28.10
reserved


28.11
reserved


28.12
reserved


Screen /

Parameter

Number
Parameter Designation

CAN / CCU diagnosis


Functional Description

Bit definition dependent on CCU type, see extra description

29.1
Status 1 (freq. Conv.)
Freq. Converter status word 1 (only Bachmann-M1 with CAN)

29.2
Status 2 (freq. Conv.)
Freq. Converter status word 2 (only Bachmann-M1 with CAN)

29.3
Error 1 (freq. Conv.)
Freq. Converter error word 1 (only Bachmann-M1 with CAN)

29.4
Error 2 (freq. Conv.)
Freq. Converter error word 2 (only Bachmann-M1 with CAN)

29.5
Error 3 (freq. Conv.)
Freq. Converter error word 3 (only Bachmann-M1 with CAN)

29.6
Error 4 (freq. Conv.)
Freq. Converter error word 4 (only Bachmann-M1 with CAN)

29.7
Error 5 (freq. Conv.)
Freq. Converter error word 5 (only Bachmann-M1 with CAN)

29.8
P grid (freq. Conv.)
Active power to grid, measured by freq. Converter (only Bachmann-M1 with CAN)

29.9
Q grid (freq. Conv.)
Reactive power to grid, measured by freq. Converter (only Bachmann-M1 with CAN)

29.10
U grid (freq. Conv.)
Grid voltage, measured by freq. Converter (only Bachmann-M1 with CAN)

29.11
I grid (freq. Conv.)
Grid current (1 phase), measured by freq. Converter (only Bachmann-M1 with CAN)

29.12
Reserved


Screen /

Parameter

Number
Parameter Designation

Scope function


Functional Description

30.1
Scope channel 1
Selection of analog signal number for Scope Ch.1 by indentifier according to “scope channel list”  (from V. 1x125)

30.2
Scope channel 2
Selection of analog signal number for Scope Ch.1 by indentifier according to “scope channel list” (from V. 1x125)

30.3
Scope channel 3
Selection of analog signal number for Scope Ch.1 by indentifier according to “scope channel list” (from V. 1x125)

30.4
Scope channel 4
Selection of analog signal number for Scope Ch.1 by indentifier according to “scope channel list” (from V. 1x125)

30.5
Time resolution
Time resolution for scope function in ms.

Max. measuring time is calculated by: 600 meas.points * time resolution

(from V. 1x125)

30.6
Pre trigger time
Pre trigger time for scope function in ms. (from V. 1x125)

30.7
Scope control
Bit0 = 1 / 0 : Start/Stop

Bit1 = 1: automatic upload of the measurement data after triggering. Upload to VisuPro second analog data (Scope Ch1..4) 

Bit2 = 1: manual upload of the measurement data after triggering. Upload to VisuPro second analog data (Scope Ch1..4) 

(Bit 2 will be reseted after the upload)

(In the time between uploads the current second values of the analog signals selected with P30.1-4 will be transmitted to VisuPro)

(from V. 1x125)

30.8
Trigger condition
No. of error message triggering the scope measurement (from V. 1x125)

30.9
Reserved


30.10
reserved


30.11
reserved


30.12
reserved


�SEITE \# "'Seite: '#'�'"  ��





t:\service\paramete\aktuell\paratw15_e2.doc
Last column indicates corresponding fault or status message number for which parameter is used

For settings see   PARA_15sxxxx.PDF 

page 1 of 1

[image: image3.wmf][image: image4.png]ENRON WIND



_1023181217.unknown

_1022478032

