14mar01

co-op city

plan forward

Item no.
Action required
Responsible party
Target completion date(s)

1
Capex – provide updated pricing numbers, including detailed scoping and schedule assumptions – i.e., what is and is not included.

· Align to enron’s mark-up of latest development agreement termsheet.





2
“cap” – provide proposed cap on capex.

· look at sensitivities on cost categories such as: major equipment, bop engineered equipment, construction bulks and labor, indirect costs, contingency, escalation, and profit (8%?).

· prepare risk book.

· Assess change in project schedule on the derivation of this “cap” number – i.e., change in cash flows.





3
O&M costs – provide updated pricing numbers, including detailed scoping assumptions – i.e., what is and is not included.

· Align to enron’s mark-up of latest development agreement termsheet?

· Align to enron’s mark-up of the latest o&m termsheet.

· Must determine/provide what is enron’s cost to provide a “not-to-exceed” guarantee on the o&m contract.

· Look at fixed component.

· Look at variable component.





4
get latest updated read from GE as to sched and cash flow requirements for gas turbines.
enron


5
get latest updated read from hrsg vendors as to sched and cash flow requirements for hrsgs.
enron


6
Project schedule – need to assess following options:

(note – co-op city to make funds application by early sep01; closing projected in oct01; with funds available in mid-nov01 timeframe.  Note – 6 year lock-out provision by state).

a) Enron locks up gas turbines and hrsgs (?) now/soon by making required payments to GE and selected hrsg vendor, respectively; paid for by co-op city should project crater.

b) Co-op city locks up gas turbines now/soon by making separate deal with GE.  Note – problematic with hrsgs; likely have to wait until funds are available in mid-nov01 timeframe.  The hrsgs are now the critical path.

c) Enron “works” the gas turbines availability issue to meet the target schedule requirements, but no guarantees.  The ordering of the hrsgs is delayed until funds are available in mid-nov01 timeframe.  The hrsgs are now the critical path.

d) The ordering of both the gas turbines and hrsgs is delayed until funds are available in mid-nov01 timeframe.  The gas turbines are the critical path.

e) Need to provide explanation as to why we no longer have a time period of 18 months from ntp to cod.





7
Project financials – i.e., what this deal means to co-op city in terms of earning/risk.  Need to provide:

· A listing of the components of the projected earnings/cash flows from ppa and asset management contracts.

· A description of the derivation of the projected earnings/cash flow from ppa and asset management contracts.

· A list of assumptions re: preceding cash flows.

· A description of what happens to cash flows/revenues in year 5 when ppa satisfied/expires.

· Provide worst case scenario numbers.  Look at several cases.  Look at for years 1 and 5 (other years?)  E.g., if unable to run lm6000 in year 5, can only run lm2500, no merchant power sales/revenue – is debt service covered?





8
Prepare 2 page summary of deal
enron
By cob 16mar01.

9
Redraft of first 4 pages of development agreement termsheet.
Co-op city
After receipt of enron’s 2 page deal summary.

10
Provide comments on enron’s mark-up of latest development agreement termsheet.
Co-op city
By cob 15mar01.

11
Co-op city to present/review cogen “deal structure” to/with state agencies/banks/financing entities.
Co-op city
Target of early to mid-apr01.

12
New york state housing finance committee to provide termsheet of co-op city’s debt refinancing.  To include/address cogen project?
N Y state
Target of mid-apr01.

13
Co-op city board to review refinancing termsheet, including cogen project.  Make go/no-go decision on enron’s involvement.
Co-op city
Target of late-apr01.

14
Meeting with con-ed.  Is load flow study needed?  Commercial vs. technical aspects.



15
Geotech work required.  Timing?



16
Conceptual design in support of permitting effort.

· timing?

· How to involve/pay for pb power’s work?





17
Preliminary design in support of prep of rfp for epc contract.

· timing?

· How to involve/pay for pb power’s work?



18
For cost plus fixed fee plus cap – use “daughter of electrobolt” contract.



19
Epc contractors – union labor:

· develop list of firms with experience in ny city.

· Meet with, discuss project and its requirements.

· Decide on competitive bid or “select and go” approach.  Has schedule and cost implications; need to assess.





20
Get emission info from GE for lm2500, lm6000 gas turbines.



21
Get bids from pb power for following work scope:

· conceptual engineering in support of permitting.

· environmental permitting.

· Geotech.

· Preliminary engineering in support of prep of rfp package for epc contract bid.

· Prep rfp package (technical and commercial)for epc contract bid.

· Evaluation/negotiation support of “pc” component of epc bid.





22
Confidentiality agreement between enron and co-op city.

· status?





23
Confidentiality agreement between enron and pb power.

· status?





24
Make sure that o&m estimate is consistent with project’s equipment lists and sizing.


















a) Listing of what enron will do:

i. Enron’s development effort includes:

1. Conceptual engineering in support of permitting.  Includes:

· major equipment selection.

· Schematic plant layout.

2. Preliminary engineering in support of prep of rfp package for epc contract.  Includes:

· Technical write-up, including:

a) Plant description.

b) Fueling systems.

c) Building system.

d) Environmental controls.

e) Utility interconnections.

· Electrical one-line drawing.

· Site plan.

· General arrangement drawing.

· Mechanical equipment list.

· Electrical equipment list.

· Heat and material balances, with guarantees.

· Quality assurance/control plan.

· Preliminary project schedule.

· Engineering calculations?

· Architectural, civil, structural engineering?

· PFDs for critical systems?

· Project execution/contracting plan?

· Project organization charts?

ii. Asset management.

iii. No fee for asset management.

iv. Development of project, not including pre-ntp cash payments for major equipment (e.g., gas turbines, hrsgs).

v. No fee for development efforts; enron will conduct at risk so long as enron gets asset management contract if project proceeds.

vi. Will assist in selection process of o&m contractor.

vii. Will provide oversight of activities of selected o&m contractor.

viii. No fee for oversight of activities of selected o&m contractor.

b) Listing of what enron will not do.

i. Enron can not be the O&m contractor (would violate accounting rules).

c) Scope:

1. Add one lm2500(dual fuel), with DLN burners, with fired hrsg (n.g. only).  With inlet chilling.  With water injection for NOx control on fuel oil.

2. Add one lm6000 (dual fuel), with DLN burners, with fired hrsg (n.g. only).  With inlet chilling.  With water injection for NOx control on fuel oil.

3. Confirm hp, ip steam, with no reheat?????

4. Which model number of gtg is correct?  Sizing?  Pricing?  Schedule delivery dates.

5. Fired hrsgs include SCR catalyst (for NOx) and CO catalyst in stacks.

6. CEMS.  One system for both stacks?

7. Two 100% (or 3 x 50%) fuel gas compressors at 700 psig.  Need to decide.

8. Refurb existing 6 mw stg (bent rotor).

9. Refurb one existing 330,000 lbs/hour high pressure (500 psig) rankine cycle boiler (leaking tubes).

10. No refurb of other 2 existing 330,000 lbs/hour low pressure rankine cycle boilers.

11. New control room for both new and existing power plant.  

12. DCS - for new and existing plant.

13. SCADA - for new and existing plant?

14. Parts storage for both new and existing power plant; to be located inside existing boiler-house where no. 3 boiler used to be.

15. Upgrade existing fuel unloading station (for no. 6 fuel) so that it can also handle no. 2 fuel oil.  Upgrades toincludefuel pumps, purification (e.g., centrifuge, duplex filters), as required.  Located to southeast of existingboilerhouse.

16. Existing n.g. connection/tie-in point located adjacent southeast corner of existing powerhouse.

17. Existing switchyard/substation located near southeast corner of existing powerhouse.

18. Proposed site has three underground condensate and circ water lines; 36 inches or 42 inches.  Potential obstruction?

19. Extend existing crane rails to east over new cogen plant to allow use of existing 35 ton crane.

20. Sufficient laydown, construction trailers, and construction parking located to north of new plant area.  Prior and current use as storage area for construction materials related to work at co-op city.  Cost estimate includes allowance for adjacent storage and construction laydown area.

21. Convert one 750k gallon fuel tank (tank no. 25) from no. 6 fuel to no. 2 fuel oil.

22. Transmission voltage equipment.

23. High generating voltage equipment.

24. Hp feedwater pumps.  6.

25. Treated water pumps.  1.

26. Raw water pumps.  2.

27. Gt lo coolant pump.  4.

28. Gt generator and gear lo coolant pump.  4.

29. Gt generator coolant pump.  4.

30. Fuel compressor coolant pump.  4.

31. St and generator lo coolant pump.  2.

32. St generator coolant pump.  2.

33. Demineralized water tank.  1.  Size?

34. Raw water tank.  1.  Size?

35. Neutralized water tank.  1.  Size?

36. Acid storage tank.  1.  Size?

37. Caustic storage tank.  1.  Size/

38. Gt lo fin fan cooler.  4.

39. Gt generator fin fan cooler.  4.

40. Chillers; for gtg inlet chilling.  Needed?????existing chillers will support gas turbine inlet chilling requirements.

41. Fuel compressor fin fan cooler.  6.

42. St and generator lo fin fan cooler.  2.

43. St generator fin fan cooler.  2.

44. Waste water treatment system.

45. Station/instrument air compressors.  2.

46. General plant instrumentation.

47. Medium voltage equipment.

48. Low voltage equipment.

49. Miscellaneous equipment.

50. Cost estimate excludes scheduled overtime and/or shift work.

51. Estimate assumes that removal and relocation of existing underground utilities by others.

52. Construction:

i. Site prep, improvements, clear laydown areas, repair/add to existing fencing as needed.

ii. Piling.

iii. Concrete and grout.

iv. Structural steel.

v. Architectural.

vi. Buildings:

a) Turbine hall; i.e., just for gtgs, with hrsgs outside.  Or power island is to be enclosed similar to existing structures (concrete and masonry brick).  ?????

b) Control room for both existing power plant and new cogen.

c) New switchgear room.

d) Locate “warehouse” inside area of former boiler no. 3 in existing boilerhouse.

vii. Painting.

viii. Mechanical piping.

ix. Insulation.

x. Erect major equipment.

xi. Bop equipment erection.

xii. Electrical.

xiii. Instrumentation.

xiv. Construction indirect costs.

xv. New york labor and productivity.

53. Utility interconnects, such as:

a) Hp steam line.

b) Make-up water/water treatment plant.

c) Boiler water.

d) Firefighting water.

54. Cost estimate based on 1 x lm2500 and 1 x lm6000.

55. Cost estimate includes escalation to mid-year????? 2002.

56. Cost numbers/allowances for rehab work included “above line” in epc cost estimate?  Excluded?

57. Cost estimates are +/- xx% accuracy.

58. Plant shutdown for tie-ins to be scheduled for contractor’s reasonable convenience.

59. Electrical tie-in to existing substation via insulated/shielded cable in open cable tray.

60. Project site is assumed to be environmentally free.

61. No “used” equipment allowed; financing constraint.  Must be new equipment.

62. No new bridge cranes.  Extend rails for use of existing boilerhouse building crane.

63. No makeup water treatment system.  Connect to existing system.  Also, during construction, need potable water trucked in?????

64. No diesel fire pump.  No jockey fire pump.  Connect to existing underground fire hydrant system.

65. No admin building.

66. No machine shop.

67. No guardhouse.

68. No 250 kw diesel generator set.  Neither black start nor emergency diesel generator capability required for the cogen plant.

69. No new auxiliary boilers (2 x 335,000 lb/hr).

70. No capital spare parts.

71. No rock excavation.

72. No o&m costs included.

73. Existing cooling tower will support new/proposed facility.

74. In case where there is low steam demand but high power demand, existing condenser is large enough to handle excess steam dump.

75. Need for interconnect fee?????

