1.	SCOPE

*	1.1	This standard covers the minimum requirements for Electronic Flow Measurement (EFM) equipment installed on the Company's pipeline system and operated by others for gas custody transfer purposes.  Any variation from this standard must be agreed to in writing by the Company.  This standard extends to and is applicable to EFM equipment installed on the Company’s system and operated by others.

*	1.2	The Company's agent responsible for negotiating and formalizing the agreement for the installation and operation of EFM equipment by others on the Company's system will also be responsible for incorporating the provisions of this standard in such agreement and will seek the approval of the Company's responsible representative for any negotiated variations from the provisions herein.  The Company's project manager or engineer responsible for the facilities where the subject EFM equipment is to be installed will be responsible for inspection and acceptance of the equipment installed by others.

*	1.3	Because of the continual technological advancement in EFM equipment and software and because compatibility among interfacing systems is critical, technical details of EFM equipment and software design are not included in this standard.  A copy of the Company’s “Specifications and Requirements for an Electronic Flow Measurement Remote Terminal Unit” is available from the Company upon request.

2.	CODES AND STANDARDS

2.1	Instruments shall be UL or FM approved for installation in the specified hazardous area classification per the NEC and shall be designed, manufactured and tested in accordance with the latest edition of the following, as applicable:

American Gas Association (AGA)

American National Standards Institute (ANSI)

American Society for Testing and Materials (ASTM)

Factory Mutual (FM)

Institute of Electrical & Electronic Engineers (IEEE)

Instrument Society of America (ISA)

National Electric Code (NEC)

National Electric Manufacturer's Association (NEMA)

Underwriters Laboratories (UL)

2.2	Use of EFM equipment which is compatible with the Company's EFM system is required.  A copy of the Company's "Specifications and Requirements for an Electronic Flow Measurement Remote Terminal Unit" is available upon request from the Company.  EFM RTU equipment must be certified by Enron Corp as an EFM device and must run the latest version of Enron Corp approved EFM software.

3.	COMPUTATIONAL AND DATA STORAGE REQUIREMENTS

*	3.1	Data storage shall be sufficient to store, on site, all data and calculated values for a minimum of 31 days.  However, if the EFM is continuously monitored, this may be reduced to 15 days storage.  Continuously monitored means than all daily data, audit trail log and event log are uploaded to the Company’s SCADA system at daily intervals for storage and any outage will be alarmed for timely remedial response.

3.2	The Company reserves the right to access the EFM data directly from the flow computer or from the data accumulation center nearest the meter site, but in no way is to interfere with operation of the EFM equipment.

4.	INPUT REQUIREMENTS

4.1	Failure of the transducer is not to be assumed when inputs overrange.  Live values are to be read as good inputs until they are manually overridden.

*	4.2	All inputs must be capable of being overridden with a fixed value during maintenance.  All such overrides will be recorded in the event log.

5.	OUTPUT REQUIREMENTS

5.1	Upon loss of power, PID loops (flow control) are to fail in current position unless specified otherwise by the Company.

5.2	Upon loss of power, meter tube must fail open or in current position unless specified otherwise by the Company.

5.3	If a continuous sampler is to be installed, a proportional-to-flow output signal from the EFM unit must be provided.

6.	STANDBY POWER REQUIREMENTS

*	6.1	For instruments monitored remotely on a continuous basis, standby power source must be installed to allow for continued volume calculations for at least 30 hours upon loss of commercial power (72 hours for Norther Border Pipeline facilities).

6.2	For instruments not monitored remotely on a continuous basis, standby power source must be installed to allow for continued volume calculations for at least 15 days upon loss of commercial power.

7.	TRANSMITTERS FOR ELECTRONIC FLOW MEASUREMENT

7.1	Maximum Transmitter Range

The maximum range of a transmitter can not exceed the operating range by more 1.5 times unless the transmitter is demonstrated to meet the accuracy specified in this standard throughout its operating range.

7.2	Sunlight Protection

All transmitters used for custody transfer measurement must be protected from prolonged direct sunlight or be compensated for or immune to temperature induced error.

7.3	Differential Pressure Transmitters

*	Provide one differential transmitter for each meter run.  All differential pressure transmitters must be located as close as possible to the orifice fitting.  Direct-mount, full-opening manifolds are preferred.  The connecting piping must be self draining and without liquid traps.  All piping and valves connecting the differential pressure transmitter to the orifice fitting should be of equal length and a constant inside diameter of at least 0.375".  Remote mounting of the transmitters is not permitted and tubing lengths should not exceed 18 inches.

*	No other instrumentation or tubing of any sort is to be connected to the differential pressure measurement flange taps.  A second set of flange taps should be provided for all other purposes.

If pulsation induced measurement errors are found to be +0.5% for volumes less than 5 MMSCF/D or +0.25% for volumes of 5 MMSCF/D or greater, it will be the responsibility of the operator to reduce the error to that level or a higher level acceptable to the Company.

7.4	Static Pressure Transmitters

*	All static pressure transmitters should be mounted as close as practical to the differential pressure transmitter using 1/4" to 3/8" tubing and the piping should be self-draining and without liquid traps.  Static pressure for turbine meters should be tubed to the pressure port for that purpose on the meter body.  A static pressure transmitter is required only on the primary meter run.  If one or more of the following conditions exist at meter stations having multiple runs, additional static pressure transmitters may be installed at the option of the measuring party.

a.	Metering pressure is below 300 PSIG.

b.	Differential pressures on any two runs differ by more than 4 inches of water column during periods when both are in service.

c.	The flowing pressures taken at the downstream taps on any two runs differ by more than 0.1%.

d.	Different types of primary measurement on any two runs.

7.5	Temperature Transmitters

A temperature transmitter is required on each run if the temperature on any two runs differ by more than 1 °F during periods when both runs are in service and gas is flowing.  All temperature probes must be installed with the probe extending into the center third of the flowing stream.

7.6	Operating Conditions

Transmitters used for custody transfer measurement shall withstand without degradation the following operating conditions:

a.	Ambient temperature of -20 °F to 140 °F,

b.	Relative humidity of 0% to 95%, non-condensing, and

c.	Overpressure to 3000 psig.

7.7	Performance Requirements

| Requirement | Low Power Transmitter | Standard or "Smart" Transmitter |
| --- | --- | --- |
| Accuracy including total effects of repeatability hysteresis & linearity | +0.25% of calibrated span | +0.1% of calibrated span |
| Temperature effects (combined zero & span) | +0.5% per 50°F of calibrated span | +0.3% per 50°F of calibrated span |
| Static pressure effects (combined zero & span) | +0.5% per 1000 psi of calibrated span | +0.3% per 1000 psi of calibrated span |

*	NOTE:  For Northern Border Pipeline facilities, only “smart” transmitters will be approved.

8.	DATA REQUIREMENTS FOR AUDIT TRAIL PURPOSES

8.1	For audit purposes the data logs and event log must be provided in one of the following formats:

8.1.1	An IBM compatible formatted disk with the Data and Event log stored in an ASCII format without editing or volume adjustments.

8..2	A hard copy print out of the Data and Event log from the flow computer without editing or volume adjustments.

8.2	All editing or volume adjustments must be kept separate from the original Data and Event Logs and a copy provided to the Company in the same manner as outlined above.

8.3	The Company shall be furnished with EFM system documentation as necessary for the Company to utilize the data supplied for audit trail purposes under this section.